SECTION 12 2400

WINDOW SHADES – LUTRON SIVOIA QS/SIVOIA QS WIRELESS

This section includes manual and motorized roller shades and associated controls featuring basis of design products from Lutron Electronics Company, Inc.

Because of the complex nature of motorized shade control systems, it is recommended that the specification and drawings be closely coordinated with consultation from the basis of design manufacturer. If systems of other manufacturers are listed or considered for substitution, the specifier should conduct a thorough evaluation to ensure that the system provides equivalent performance and that other related products will interface properly.

This section includes accessories for standalone occupant control of motorized window shades.

See Section 12 2509.13 (12498) - Window Shade Control System - Lutron Hyperion for Lutron's Hyperion solar adaptive control system for window shades only (no lights).

See the following Lutron sections for systems capable of controlling both lights and shades:

• Section 26 0936 (16573) – Modular Dimming Controls – Lutron QS.

• Section 26 0943 (16575) - Network Lighting Controls – Lutron Quantum.

• Section 26 0943 (16575) – Network Lighting Controls – Lutron HomeWorks.

• Section 26 0943 (16575) – Network Lighting Controls – Lutron Athena.

• Section 26 0995 (16595) – Hotel Guestroom Controls – Lutron myRoom.

SECTION 12 2400 (12490) - WINDOW SHADES – LUTRON SIVOIA QS/SIVOIA QS WIRELESS, Copyright 2015-2021, Lutron Electronics Company, Inc.

- GENERAL

  - SECTION INCLUDES

    - Motorized roller shades.

    - Manual roller shades, to match motorized shades.

    - Shade accessories.

    - Motorized shade controls.

  - RELATED REQUIREMENTS

    - Section 06 1000 - Rough Carpentry: Concealed wood blocking for attachment of headrail brackets.

    - Section 09 2116 - Gypsum Board Assemblies: Substrate for window shade systems.

    - Section 09 5100 - Acoustical Ceilings: Shade pockets, pocket closures and accessories.

Lutron offers brackets with wire management compatible with Armstrong AXIOM Building Perimeter System integrated shade pocket/closures.

    - Section 095113 – Perimeter Transition System:  Shade pockets, pocket closures and accessories.

    - Section 12 2509.13 - Window Shade Control System – Lutron Hyperion: Automated solar adaptive control system for motorized window shades.

    - Section <<______>>: Building automation system, for interface with shade controls.

    - Section 26 0553 - Identification for Electrical Systems: Identification products and requirements.

    - Section 26 0936 – Modular Dimming Controls – Lutron QS: Lighting control system for control of motorized window shades.

    - Section 26 0943 - Network Lighting Controls – Lutron Quantum: Lighting control system for control of motorized window shades.

    - Section 26 0943 - Network Lighting Controls – Lutron HomeWorks: Lighting control system for control of motorized window shades.

    - Section 26 0943 - Network Lighting Controls – Lutron Athena: Lighting control system for control of motorized window shades.

    - Section 26 0995 – Hotel Guestroom Controls – Lutron myRoom:  Hotel guestroom control system for control of motorized window shades.

    - Section 26 2726 - Wiring Devices - Lutron:

      - Finish requirements for wall controls specified in this section.

      - Accessory receptacles and wallplates, to match shade controls specified in this section.

    - Section <<______>>: Audio-video systems, for interface with shade controls.

  - REFERENCE STANDARDS

    - ASTM D4674 - Standard Practice for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Office Environments; 2002a (Reapproved 2010).

    - ASTM E308 - Standard Practice for Computing the Colors of Objects by Using the CIE System; 2017.

    - ASTM E903 - Standard Test Method for Solar Absorptance, Reflectance, and Transmittance of Materials Using Integrating Spheres; 2012.

    - DIN EN 14500 - Blinds and Shutters - Thermal and Visual Comfort - Test and Calculation Methods; 2008.

    - IEC 61000-4-2 - Electromagnetic Compatibility (EMC) - Part 4-2: Testing and Measurement Techniques - Electrostatic Discharge Immunity Test; 2008.

    - ISO 9001 - Quality Management Systems-Requirements; 2008.

    - NECA 1 - Standard for Good Workmanship in Electrical Construction; 2015.

    - NECA 130 - Standard for Installing and Maintaining Wiring Devices; National Electrical Contractors Association; 2010.

    - NEMA WD 1 - General Color Requirements for Wiring Devices; National Electrical Manufacturers Association; 1999 (R 2015).

    - NFPA 70 - National Electrical Code; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.

  - ADMINISTRATIVE REQUIREMENTS

    - Coordination:

      - Where motorized shades are to be controlled by control systems provided under other sections, coordinate the work with other trades to provide compatible products.

      - Coordinate the work with other trades to provide rough-in for electrical wiring as required for installation of motorized shades.

      - Notify Architect of any conflicts or deviations from the contract documents to obtain direction prior to proceeding with work.

    - Preinstallation Meeting: Conduct on-site meeting with shade control system installer prior to commencing work to review:

      - Low voltage wiring requirements.

      - Separation of power and low voltage/data wiring.

      - Wire labeling.

      - Control locations.

      - Connections to other equipment.

      - Installer responsibilities.

      - Pocket and/or mounting conditions.

    - Sequencing:

      - Do not fabricate shades until field dimensions for each opening have been taken.

      - Do not install shades until final surface finishes and painting are complete.

      - Do not install wall controls until final surface finishes<< and painting>> are complete.

  - SUBMITTALS

    - See Section 01 3000 - Administrative Requirements, for submittal procedures.

    - Product Data: Provide manufacturer's standard catalog pages and data sheets including materials, finishes, fabrication details, dimensions, profiles, mounting requirements, and accessories.

      - Motorized Shades: Include power requirements and standard wiring diagrams.

    - Shop Drawings:

      - Include <<shade schedule indicating size, location and keys to details; head, jamb and sill details; mounting dimension requirements for each product and condition; operation direction; and __________>>.

      - Motorized Shades:

        - Provide schematic system riser diagram indicating component interconnections. Include requirements for interface with other systems.

        - Provide shade drive layout drawing showing locations of shade drives, power supplies, and sensor modules.

    - Certificates: Manufacturer's documentation that line voltage components are UL listed or UL recognized.

    - Test Reports: Indicating compliance with specified fabric properties.

    - Samples:

      - Shade Fabric: Showing <<specified colors and patterns; manufacturer's full range of available colors and patterns; or _________>>.

      - Motorized Shade Controls: Show available color and finish selections.

    - Manufacturer's Installation Instructions: Include application conditions and limitations of use stipulated by product testing agency. Include instructions for storage, handling, protection, examination, preparation, and installation of product.

    - Project Record Documents: Record actual installed locations and settings for shade control system components.

    - Operation and Maintenance Data: List of all components with part numbers, sources of supply, and operation and maintenance instructions; include copy of shop drawings.

    - Warranty: Submit sample of manufacturer's warranty and documentation of final executed warranty completed in Owner's name and registered with manufacturer.

  - QUALITY ASSURANCE

    - Conform to requirements of NFPA 70.

    - Maintain at the project site a copy of each referenced document that prescribes execution requirements.

    - Manufacturer Qualifications:

      - Company with not less than twenty years of experience manufacturing low voltage motorized shading systems.

      - Registered to ISO 9001, including in-house engineering for product design activities.

      - Qualified to supply specified products and to honor claims against product presented in accordance with warranty.

    - Shade Installer Qualifications: Qualified to install and commission specified products by prior factory training, experience, demonstrated performance, and acceptance of any requirement of the manufacturer, subsidiary of the manufacturer, or licensed agent.

  - MOCK-UP

    - Mock-Up: Provide<< full size; minimum 2 ft wide by 3 ft high ( minimum 0.60 m wide by 0.94 m high); minimum __ ft wide by __ ft high ( minimum __ m wide by __ m high);or  ______>> << operable shade; fixed fabric panel only; or  ______>> mock-up of window shade << in pocket/closure>> complete with selected shade fabric including sample of seam when applicable.

Mock-up is good for viewing the aesthetics and control functionality within the space. Mock-up is not sufficient for evaluating glare, daylighting, and view performance due to seasonal variability and environmental change. It is recommended that an annual daylighting simulation is performed using software, such as the Performance Shading Advisor (www.performanceshadingadvisor.com).

      - Obtain Architect's approval of aesthetics and control functionality prior to fabrication.

--CHOOSE ONE OF THE TWO PARAGRAPHS BELOW IF FULL-SIZED OPERABLE SHADE MOCK-UP IS SPECIFIED ABOVE--

      - Full-sized, operable shade mock-up may become part of the final installation.

      - Full-sized, operable shade mock-up will become the property of the Owner to be used for spare parts.

      - Mock-ups incorporating pocket/closure to represent roll-up diameter of shade for tallest window.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver shades in manufacturer's unopened packaging, labeled to identify each shade for each opening.

    - Handle and store shades in accordance with manufacturer's recommendations.

  - FIELD CONDITIONS

    - Maintain field conditions within manufacturer's required service conditions during and after installation.

      - Basis of Design System Requirements, Unless Otherwise Indicated:

        - Ambient Temperature: Between 32 and 104 degrees F (0 and 40 degrees C).

        - Relative Humidity: Less than 90 percent, non-condensing.

  - WARRANTY

    - See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

    - Manufacturer's Warranty:

      - Shade Control System Components (including shade electronic drive units, shade fabric, and shade hardware):

        - Years 1-5: 100 percent replacement parts coverage, no manufacturer labor coverage.

        - Years 6-8: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

      - External Shade Control System Components (including control stations, interfaces, and system accessories):

        - One year 100 percent replacement parts coverage, 100 percent manufacturer labor coverage to troubleshoot and diagnose a shade control issue.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

- PRODUCTS

  - MANUFACTURERS

    - Basis of Design Manufacturer: Lutron Electronics Company, Inc; www.lutron.com.

    - Other Acceptable Manufacturers:

      - <<______>>.

      - <<______>>.

      - <<______>>.

      - Products by listed manufacturers are subject to compliance with specified requirements<< and prior approval of Architect; or _________>>.

    - Substitutions: <<See Section 01 6000 - Product Requirements; Not permitted; or __________>>.

      - All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by Architect a minimum of <<10; or _____>> working days prior to the bid date and must be made available to all bidders. Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

      - Any proposed substitutions to be reviewed by Architect at Contractor's expense<< at a rate of $200 per hour; at a rate of _________; or __________>>.

      - By using pre-approved substitutions, Contractor accepts responsibility and associated costs for all required modifications to related equipment and wiring. Provide complete engineered shop drawings (including power wiring) with deviations from the original design highlighted in an alternate color for review and approval by Architect prior to rough-in.

    - Source Limitations:

      - Furnish products produced by a single manufacturer and obtained from a single supplier.

      - Manual Shades: Produced by the same manufacturer as the motorized shades, to match appearance.

      - Furnish products produced by the same manufacturer as the window shade control system as specified in Section 12 2509.

      - Furnish products produced by the same manufacturer as the lighting control system as specified in Section <<26 0936; 26 0943; 26 0995; or __________>>.

Lutron's new web-based Performance Shading Advisor transforms the complicated task of choosing fabrics into a simple selection process. This innovative daylight simulation tool makes it easy to optimize shading system design based on building performance and aesthetic preference. Reduce glare, maximize daylight, preserve view, and enhance your design at www.performanceshadingadvisor.com.

  - WINDOW SHADE FABRIC APPLICATIONS

    - Fabric for Roller Shades:

      - Solar Screen Fabric:

        - Color:  <<______>>.

--CHOOSE ONE OF THE FOLLOWING TWO PARAGRAPHS WHERE APPLICABLE--

          - Custom Printing: Artwork to be provided by Architect.

          - Custom Printing: Artwork to be selected from manufacturer's collection.

--COPY AND EDIT THE FOLLOWING FOR EACH UNIQUE FACADE—

        - Façade/Orientation Name:  <<______>>.

--CHOOSE ONE OF THE FOLLOWING TWO OPTIONS BASED ON FABRIC SELECTED--

Today, the typical industry tolerances around fabric solar performance properties is large and can cause reduced visual comfort and energy savings. Actual performance may vary by plus/minus 2 percent or more in openness factor. If fabric performance properties are not tightly controlled, your building design intent will not be achieved. For performance critical applications, specify Specification Grade Solar Screens, or Lutron's THEIA™ Compliant fabrics.

          - Fabric Performance Requirements – Spec Grade Solar Screen (THEIA Compliant):

            - Openness Factor:  <<______>>.

            - Openness Factor Tolerance:  <<______>>.

            - Visible Light Transmittance (Tv):  <<______>>.

            - Visible Light Transmittance (Tv) Tolerance:  <<______>>.

            - Solar Transmittance (Ts):  <<______>>.

            - Solar Absorption (As):  <<______>>.

            - Solar Reflectance (Rs):  <<______>>.

          - Fabric Performance Requirements – General Purpose/Sustainable Solar Screen:

            - Openness Factor:  <<______>>.

            - Visible Light Transmittance (Tv):  <<______>>.

--INCLUDE THE FOLLOWING PROPERTIES WHERE APPLICABLE--

            - Solar Transmittance (Ts):  <<______>>.

            - Solar Absorption (As):  <<______>>.

            - Solar Reflectance (Rs):  <<______>>.

--INCLUDE OTHER REQUIRED PROPERTIES BELOW WHERE APPLICABLE--

        - Other Fabric Properties:

          - Fire Rating:  <<______>>.

Use the following paragraph to specify fabric material composition requirements (e.g. PVC free, 100% recycled content polyester, PVC coated fiberglass, etc).

          - Material Composition:  <<______>>.

Use the following paragraph to specify required fabric certifications (e.g. GREENGUARD, PVC free, Cradle-to-Cradle, Oeko-Tex, RoHS, Anti-Microbial, etc).

          - Required Certifications:  <<______>>.

Use the following paragraph to specify other required fabric properties (e.g. Railroadable, Dual-sided, Seamable, Maximum Usable Width, etc).

          - <<______>>.

--ONLY INCLUDE THE FOLLOWING FOR DUAL MOUNTED SHADES (TWO FABRIC TYPES IN ONE OPENING)--

      - Blackout Fabric:

        - Color:  <<______>>.

--CHOOSE ONE OF THE FOLLOWING TWO PARAGRAPHS WHERE APPLICABLE--

          - Custom Printing: Artwork to be provided by Architect.

          - Custom Printing: Artwork to be selected from manufacturer's collection.

--COPY AND EDIT THE FOLLOWING FOR EACH UNIQUE FACADE—

        - Façade/Orientation Name:  <<______>>.

          - Fabric Performance Requirements:

            - Openness Factor:  <<______>>.

--INCLUDE THE FOLLOWING PROPERTIES WHERE APPLICABLE--

            - Solar Absorption (As):  <<______>>.

            - Solar Reflectance (Rs):  <<______>>.

--INCLUDE OTHER REQUIRED PROPERTIES BELOW WHERE APPLICABLE--

        - Other Fabric Properties:

          - Fire Rating:  <<______>>.

Use the following paragraph to specify fabric material composition requirements (e.g. PVC free, 100% recycled content polyester, PVC coated fiberglass, etc).

          - Material Composition:  <<______>>.

Use the following paragraph to specify required fabric certifications (e.g. GREENGUARD, PVC free, Cradle-to-Cradle, Oeko-Tex, RoHS, Anti-Microbial, etc).

          - Required Certifications:  <<______>>.

Use the following paragraph to specify other required fabric properties (e.g. Railroadable, Dual-sided, Seamable, Maximum Usable Width, etc).

          - <<______>>.

    - Solar Screen Fabric General Requirements:

      - Fabric Performance Selection:

        - Fabrics must be selected based on evaluation using a building model.

        - Model must incorporate location, facade orientation(s), window size(s), glass properties, and interior layout and properties.

        - Submit report documenting glare, daylight, and view performance results.

--ONLY INCLUDE THE FOLLOWING IF SPEC GRADE SOLAR SCREEN (THEIA™ COMPLIANT) FABRIC IS SPECIFIED ABOVE--

Today, the typical industry tolerances around fabric solar performance properties is large and can cause reduced visual comfort and energy savings. Actual performance may vary by plus/minus 2 percent or more in openness factor. If fabric performance properties are not tightly controlled, your building design intent will not be achieved. For performance critical applications, specify Specification Grade Solar Screens, or Lutron's THEIA™ Compliant fabrics.

      - Fabric Performance Assurance - Spec Grade Solar Screen (THEIA™ Compliant):

        - Measurement Standards:

          - Openness Factor:  DIN EN 14500.

          - Visible Light Transmittance (Tv):  ASTM E903.

        - Statistical Validation Level:

          - Verify with a 95 percent confidence level that 95 percent of all fabric from rolls in the manufacturing lot are within the tolerance bounds (stated above).

          - Equivalent to Statistical PPK greater than or equal to one, when all rolls of fabric in the lot are evaluated using a minimum of twenty samples.

        - Certification Documentation:

          - All rolls of fabric must be certified to comply with the Fabric Performance Requirements (stated above).

          - Provide documentation with each roll verifying that the statistical requirements for fabric tolerance are met for all rolls of fabric in the manufacturing lot.

          - Upon request, fabric supplier must be able to trace certification and statistical documentation back to the original lot sample.

  - ROLLER SHADES

    - Roller Shades: Fabric roller shades complete with mounting brackets, roller tubes, hembars, hardware and accessories; fully factory-assembled.

Fabric drop options are: regular roll (fabric on the glazing side of the roller), and reverse roll (fabric on the room side of the roller).

      - Drop: <<Regular roll; Reverse roll; or _____>>.

      - Size: <<As indicated on drawings; ___ inches wide by ___ inches high (___ mm wide by ___ mm high); or _________>>.

    - Roller Tube: As required for type of operation.

      - Size: Manufacturer's standard, selected for suitability for installation conditions, span, and weight of shades.

      - Size: <<_____>> inch (<<_____>> mm).

      - Fabric Attachment: Utilize double-sided adhesive strip with minimum of one turn of fabric on roller before working section of fabric starts.

    - Hembars: Wall thickness designed for weight requirements and adaptation to uneven surfaces, to maintain bottom of shade straight and flat.

Verify compatibility of hembar with fabric selected.

      - Style: <<Architectural half wrap; Architectural exposed; 1 inch exposed with light-blocking wool pile; Sealed; Oval; Designer; or ______>>.

      - Color/Finish: <<White; Bronze; Black; Silver; As selected from manufacturer's standard colors; or _____>>.

      - Endcaps: Color to coordinate as recommended by manufacturer.

    - Motorized Shades: Electronic drive unit concealed from view inside roller tube, controlling shade movement via motor controls indicated; fully compatible with the controls to be installed.

      - Product(s):

Include the following paragraph for Lutron Sivoia QS shades.

        - Low-voltage wired shades with wired (low voltage) communications.

Include the following paragraph for Lutron Sivoia QS Wireless shades.

        - Low-voltage wired shades with integrated wireless (RF) communications.

Noise rating is measured with the largest shade in the heaviest fabric.

      - Audible Noise: Capable of operating at or below 38 dBA measured 3 feet (1 m) from center of the shade depending on the electronic drive unit selected; no audible clicks when motor starts and stops.

      - Electronic Drive Units:

        - Low voltage, for connection to NFPA 70, Class 2 power source.

        - Size and configuration as recommended by manufacturer for the type, size, and arrangement of shades to be operated.

      - Integrated Wireless Communications: Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

Angular coupling can operate up to three panels in angular application of 45 degrees or less. In-line coupling allows a single drive to operate up to six panels. Verify coupling capabilities with manufacturer.

      - Coupling of Multiple Shades:

        - Where possible, minimize number of electronic drive units by coupling adjacent shades.

        - Utilize coupling pin that allows for precision adjustment of bottom bar levels without removing roller from installed point or fabric from roller tube.

    - Manual Shades: To match motorized shades, by same manufacturer; <<clutch operated continuous loop, beaded ball chain, clutch size as recommended by manufacturer for weight of fabric; cordless operation; or __________>>.

  - SHADE ACCESSORIES

Verify bracket compatibility with size and type shade specified.

    - Brackets and Mounting Hardware: Size as recommended by manufacturer for mounting configuration and span indicated.

      - Universal mounting bracket.

      - Two-piece adjustable mounting bracket.

      - Dual bracket for two shades mounted in same opening.

Lutron offers brackets with wire management compatible with Armstrong AXIOM Building Perimeter System integrated shade pocket/closures.

      - Bracket with wire management for compatible integrated shade pocket/closure as specified in Section 09 5113.

    - Fasteners: Non-corrosive, and as recommended by shade manufacturer.

    - Fascia<< with top back cover>>: Size as required to conceal shade mounting.

      - Style: <<Square; Curved; As indicated on the drawings; or ______>>.

      - Color/Finish: <<White; Black; Bronze; Silver; To match shade fabric; or ______>>.

    - Pocket: Manufacturer's <<standard; custom; or _____>> 0.06 inch (1 mm) thick minimum aluminum pocket for recessed mounting.

      - Provide <<cover flap; integrated air vents; ceiling tile support; splice bar; and _____>>.

      - Size: <<_____>> inch width by <<____>> inch height (<<_____>> mm width by <<____>> mm height).

Include the following paragraph for a light seal where light-blocking fabric is used and complete blackout is required.

    - Light-Sealing Accessories for Blackout Shades: Provide <<sill angles; side channels; and _________>> to complete light seal.

      - Color/Finish: <<White; Bronze; Black; Light ivory; Taupe; Slate grey; Clear anodized aluminum; As selected from manufacturer's standard colors; or _____>>.

  - MOTORIZED SHADE CONTROLS

--CHOOSE ONLY ONE OF THE FOLLOWING THREE PARAGRAPHS--

Include the following paragraph if shades are to be controlled by Lutron's Hyperion automatic solar-tracking window shade control system specified in Section 12 2509 (for control of shades only, no lights). Then omit the remainder of this article and proceed to article SHADE FABRICATION.

    - Motorized shades to be controlled by automated solar adaptive window shade control system and associated control devices as specified in Section 12 2509.

Include the following paragraph if shades are to be controlled by a Lutron lighting control system specified in another section. Then omit the remainder of this article and proceed to article SHADE FABRICATION.

    - Motorized shades<<, unless otherwise indicated,; for __________;, where indicated,; or _________>> to be controlled by lighting control system and associated control devices as specified in Section <<26 0936;26 0943; 26 0995; or __________>>.

Include the following paragraph if controls for motorized shades are to be specified in this section.

    - Motorized shades<<, unless otherwise indicated,;, where indicated,; for _________; or __________>> to be controlled by control stations and associated accessories as specified below.

    - General Requirements:

      - Provide products listed, classified, and labeled by Underwriter's Laboratories Inc. (UL) as suitable for the purpose indicated.

      - Unless specifically indicated to be excluded, provide all required equipment, conduit, boxes, wiring, connectors, hardware, supports, accessories, software, system programming, etc. as necessary for a complete operating system that provides the control intent indicated.

      - System Capacity:

        - Supports up to 100 wired devices including shades, control stations, and power supplies.

        - Supports wireless devices within range of the wireless control.

        - Supports up to 100 wired zones.

      - Shade Control Requirements:

        - Capable of operating shades and recalling shade presets via keypad, contact closure input, infrared receiver, lighting management system software, or other lighting control system interface.

        - Capable of operating any individual, group, or subgroup of shade electronic drive units within system without requiring separate group controllers.

        - Capable of assigning and reassigning individual, groups, and subgroups of shades to any control within system without requiring additional wiring or hardware changes.

        - Capable of controlling shade speed for tracking within plus or minus 0.125 inch (3.17 mm) throughout entire travel.

        - Provide 10 year power failure memory for preset stops, open and close limits, shade grouping and subgrouping and system configuration.

        - Capable of synchronizing multiple shade electronic drive units to start, stop, and move in unison.

        - Capable of stopping shades within accuracy of 0.125 inch (3.17 mm) at any point between open and close limits.

        - Capable of storing up to 250 programmable stop points, including open, close, and any other position.

Include this paragraph to ensure that the operating equipment is designed to operate at worst case environmental conditions without affecting product life.

      - Design shade control equipment for 10 year operational life while operating continually at any temperature in an ambient temperature range of 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C) and 90 percent non-condensing relative humidity.

      - Electrostatic Discharge Tolerance: Design and test equipment to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

      - Device Finishes:

        - Wall Controls: <<Match finishes specified for wiring devices in 26 2726, unless otherwise indicated; As indicated on the drawings; To be selected by Architect; or __________>>.

        - Standard Colors: Comply with NEMA WD1 where applicable.

        - Color Variation in Same Product Family: Maximum delta E of 1, CIE L*a*b color units per ASTM E308.

Daylight or fluorescent lighting generate ultraviolet light which can cause parts that do not meet ASTM D4674 to discolor/yellow over time.

        - Visible Parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

      - Provide all components and connections necessary to interface with other systems as indicated.

    - Keypads:

      - General Requirements:

        - Allows control of any devices part of the shade control system.

Controls can be programmed with different functionality through system software without any hardware changes.

        - Allows for easy reprogramming without replacing unit.

        - Buttons/Engraving:

To help occupants understand how to use the shade control system, engraving requirements should be included for all controls. Engraving details should include text size and style.

          - Engrave keypads with button, zone, and scene descriptions <<as indicated on the drawings; to be selected by Architect; or _________>>.

Engraving must be durable when exposed to cleaning and normal wear.

          - Borders, logos, and graduations to use laser engraving or silk-screened graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

Unlike traditional scene control wall stations, centralized low voltage controls can be programmed so that the buttons can have a variety of functions.

        - Software Configuration:

          - Customizable control station device button functionality:

            - Buttons can be programmed to perform single defined action.

            - Buttons can be programmed to perform defined action on press and defined action on release.

        - Status LEDs:

Time delays inherent in large systems can cause short delays between button press and system confirmation. To avoid any confusion and prevent multiple button presses, keypads should immediately show that the button has been pressed for visual confirmation.

          - Upon button press, LEDs to immediately illuminate.

There are two types of keypads; those that only send signals and those that send and receive signals. Having the latter type allows feedback to the user to verify that the request has been received and processed. If the shade control system fails to process the button press request, the LED will turn off to indicate the true system status.

          - LEDs to reflect the true system status. LEDs to remain illuminated if the button press was properly processed or LEDs to turn off if the button press was not processed.

          - Support logic that defines when LED is illuminated:

            - Scene logic (logic is true when all zones are at defined levels).

            - Last scene (logic is true when spaces are in defined scenes).

seeTouch QS Keypads::

• Available in several button configurations and finishes

• Receive up to two contact closure inputs

• LEDs on each button are used during programming and provide feedback when the buttons are pressed

• Large, rounded, backlit buttons with optional engraving

      - Wired Keypads:

Architectural series keypads use Lutron Nova T* wall plates and are available in insert and non-insert styles. International series keypads use Lutron International style wall plates and are available in insert and non-insert styles. The insert style allows decorator-style controls to be easily ganged. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox or low-voltage mounting bracket; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Provide integral infrared receiver for personal control<< where indicated; or _________>>.

        - Finish: <<As specified for wall controls in "Device Finishes" under General Requirements above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Architrave Keypads:

• Available in several button configurations and finishes

• Receives up to two contact closure inputs

• LEDs next to each button are used during programming and provide feedback when the buttons are pressed

• Available with green status and backlight LEDs

      - Wired Keypads:

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under General Requirements above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Signature Series Keypads:

• Available in several button configurations and finishes

• Receive up to two contact closure inputs

• LEDs on each button are used during programming and provide feedback when the buttons are pressed

• Large, rounded, backlit buttons with option engraving

• Available with either Green or Blue status and backlight LEDs

      - Wired Keypads:

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under General Requirements above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

The following is based on Lutron Sivoia QS Wireless seeTouch keypads.

      - Wireless Keypads:

        - Power: 120 VAC, 60 Hz; provide connection as indicated or as required.

        - Communications: Communicates via radio frequency to compatible window treatments.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:  Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Finish: <<As specified for wall controls in "Device Finishes" under General Requirements above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

The versatile design of Sivoia QS Wireless seeTouch Tabletop Keypads allows them to be mounted on a wall, placed on top of a table, or used as a cordless Keypad. The Keypads can be powered by the DC adapter provided with the Keypad or with 2 AAA batteries. Battery powered Tabletop Keypads will shut off after a short period of inactivity in order to conserve battery power.

      - Wireless Tabletop Keypads:

        - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

        - Power: Furnished with provisions for both battery operation and plug-in connection to standard 120 VAC receptacle via supplied DC adapter.

        - Communications: Communicates via radio frequency to compatible window treatments.

        - Mounting: Suitable for use as a tabletop or handheld remote; provide accessory bracket for optional wall-mounting.

        - Button/Engraving Backlighting:  Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

        - Design keypads to shut off after a short period of inactivity when operating on battery power.

          - "Wake-Up Only": Single button press to "wake-up" keypad and show status; subsequent press to activate button.

        - Finish: << As indicated on drawings; To be selected by Architect; or __________>>.

The following is based on Lutron QS Keyswitch.

    - Wired Keyswitch:

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Configuration:

        - <<Type _____ - >>Three position, momentary, center position key removal.

        - <<Type _____ - >>Three position, maintained, center position key removal.

        - <<Type _____ - >>Two position, maintained, center position key removal.

        - <<Type _____ - >>Two position, maintained, any position key removal.

      - Allows control of any devices part of the shade control system.

      - Power: Class 2 (low voltage).

      - Communications:  Utilize RS485 wiring for low-voltage communications link.

      - Functionality:

Controls can be programmed with different functionality through system software without any hardware changes.

        - Allows for easy reprogramming without replacing unit.

        - Requires key insertion to activate actions.

To help building occupants understand how to use the lighting control system, engraving requirements should be included for all controls. Engraving details should include text size and style.

      - Engrave wall stations with button, zone, and scene descriptions <<as indicated on the drawings; to be selected by Architect; or _________>>.

      - Software Configuration:

        - Customizable control station device button functionality:

          - Key positions can be programmed to perform single defined action.

      - Finish: <<As specified for wall controls in "Device Finishes" under General Requirements above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

    - Wireless (Radio Frequency) Controls:

The Pico Wireless Control is a flexible and easy to use device that allows the user to control shades. The Pico wireless control can function as a tabletop control on a pedestal, a lightweight handheld remote, or it can be wall-mounted with or without a Lutron Claro faceplate, to mimic a traditional keypad. The battery-operated control requires no external power or communication wiring. Pico wireless controls can be utilized with wired (requires QS sensor module), battery-powered and wireless shades.

      - Product(s):

        - <<Type _____ - >>2-Button with Raise/Lower Control.

          - Button Marking:  <<Shade (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control.

          - Button Marking:  <<Shade (text); Shade (icons); Blackout (text); Sheer (text); As indicated on drawings; or __________>>.

        - <<Type _____ - >>4-Button.

          - Button Marking:  <<Zone controls (shade); Scene keypads (shade); 2-group controllers (shades); As indicated on drawings; or __________>>.

        - Single Pedestal.

        - Double Pedestal.

        - Triple Pedestal.

        - Quadruple Pedestal.

        - Screw Mounting Kit.

        - Wallplate Adapter.

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Communicates via radio frequency to compatible window treatments.

      - Does not require external power packs, power or communication wiring.

      - Allows for easy reprogramming without replacing unit.

      - Single action button programming. Includes LED to indicate button press or programming mode status.

      - Mounting:

        - Capable of being mounted with a table stand or directly to a wall under a faceplate.

        - Faceplates: Provide concealed mounting hardware.

      - Power: Battery-operated with minimum ten-year battery life.

      - Finish: <<As specified for wall controls in "Device Finishes" under General Requirements above; As indicated on drawings; White; Black; Ivory; Light Almond; White/Gray; or __________>>.

The following is based on Lutron CS-YJ-4GC-WH.

    - 4-Group Radio Frequency Handheld Control:

      - Provides open/close, raise/lower, and preset control for up to four shade groups; backlit buttons indicate which shade group is selected.

      - Power:  Battery-operated with average seven-year battery life.

      - Communications:  Communicates via radio frequency to compatible window treatments.

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Finish: White.

Infrared transmitters are used with Lutron-supplied infrared receiver controls. They are used in spaces where remote control is required. Operation is through line-of-sight.

    - Infrared Handheld Controls (Requires Infrared Receiver):

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Product(s):

        - <<Type _____ - >>4-Button Transmitter with Open/Close and Raise/Lower Control.

        - <<Type _____ - >>5-Button Transmitter with Open/Close, Raise/Lower Control, and Preset for Single Shade Group.

          - Button Marking: <<Shade; As indicated on drawings; or _________>>.

        - <<Type _____ - >>10-Button Transmitter with Open/Close, Raise/Lower Control, and Preset for Two Shade Groups.

          - Button Marking: <<Shade 1 and Shade 2; Screen and Blackout; Sheer and Blackout; As indicated on drawings; or _________>>.

        - <<Type _____ - >>Transmitter with 3 Presets, Open/Close, and Fine Tune Raise/Lower Control.

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Finish: White.

The following is based on Lutron Model QSGR-TC-3S-WH-CPN5825.

    - Timeclock:

      - Allows set up of shade presets using buttons on control unit.

      - Built-in Astronomical Timeclock:

        - 7 day schedules available.

        - One available holiday schedule is programmable by date up to one year in advance.

        - 25 events per day maximum.

        - Astronomic times are programmable by integral city database or entering latitude and longitude. Time automatically adjusts throughout the year based on location.

        - Automatically adjusts for Daylight Savings Time (DST), adjusted for the new dates; DST is programmable.

        - Afterhours feature allows occupants to temporarily override timeclock events.

      - Preset Shade Control:

        - Three columns of shade controls.

        - Open, preset, close, and raise/lower shade buttons.

        - Each shade column can be programmed to operate one shade or a group of shades.

      - Contact Closure Input (CCI):

        - Capable of operating in the following modes:

          - Afterhours: Allows the CCI to start and end the afterhours mode.

          - Timeclock:  Allows the CCI to enable and disable the timeclock.

          - Disable CCI:  CCI will have no effect on the system and will not appear on the list of available sensors.

          - Security lockout via password for timeclock settings.

These interfaces enable the shade control system to receive or send a control signal to or from another system (Partitioning, Occupancy, A/V, BMS). Include this article if control over the system through external inputs such as contact closure, Ethernet, RS232, building management systems (BMS), etc. is required.

    - Low-Voltage Control Interfaces:

      - Provide low-voltage control interfaces as indicated or as required to control the loads as indicated.

      - UL listed.

The following is based on Lutron Model QSE-IO.

      - Contact Closure Interface:

        - The contact closure input device to accept both momentary and maintained contact closures.

        - The contact closure output device can be configured for maintained or pulsed outputs.

        - Contact closure can be programmed using conditional logic off of a state variable such as time of day or partition status.

The following is based on Lutron Model QSE-CI-WCI.

      - Wallbox Input Closure Interface:

        - Mounts in wallbox behind contact closure keypad to provide interface for up to eight contact closure inputs.

        - The contact closure input device to accept both momentary and maintained contact closures.

The following is based on Lutron Model QSE-CI-NWK-E.

      - RS232 and Ethernet Interface:

        - Provide ability to communicate via Ethernet or RS232 to audiovisual equipment, touchscreens, etc.

        - Provide control of:

          - Shade group presets.

          - Fine-tuning of shade preset levels with raise/lower.

          - Simulate system wall station button presses and releases.

        - Provide status monitoring of:

          - Shade group status.

          - Wall station button presses and releases.

          - Wall station LEDs.

The QS Sensor Module (QSM) is a ceiling-mounted device that integrates Lutron wireless and wired controls through the QS communication link to Sivoia QS shades.

      - Sensor Modules:

        - Products:

Capabilities of the following module:

Maximum of 10 wireless controllers

Sensor Module wireless range:

60 ft (18 m) line of sight

30 ft (9 m) through walls

          - Sensor module with both wired and wireless inputs.

Capabilities of the following module:

Maximum of 10 wireless controllers

Sensor Module wireless range:

60 ft (18 m) line of sight

30 ft (9 m) through walls

          - Sensor module with wireless inputs only.

        - Wireless Modules:

          - Provide wireless communication inputs for:

            - Wireless controller.

          - RF Range: 30 feet (9 m) between sensor and compatible RF receiving devices.

          - RF Frequency: 434 MHz; operates in FCC governed frequency spectrum for periodic operation; continuous transmission spectrum is not permitted.

        - Communicate sensor information to wired low-voltage digital link for use by compatible devices.

The following is based on Lutron Model QSE-IR-WH.

      - Infrared Receiver:

        - Permits IR integration via infrared handheld controls or third party IR remotes.

        - Utilizes self-adhesive mounting disc for secure mounting to any surface.

    - Power Supplies: Provide as indicated or as required to power system devices and accessories.

      - Product(s):

The following is based on Lutron Model QSPS-J-1-35V.

        - Junction box-mounted power supply for shades, keypads, and accessories, and for providing additional low voltage power to communication link; with miswire and thermal protection.

The following is based on Lutron Model QSPS-P1-1-35V.

        - Plug-in power supply for shades, keypads, and accessories, and for providing additional low voltage power to communication link; with miswire protection; powered from standard receptacle using cord 6 feet (1.8 m) in length; complies with DOE Level VI regulation.

The following is based on Lutron Model QSPS-10PNL-NPM (10-output configurable smart enclosure), Model QSPS-30PNL-NPM (30-output configurable smart enclosure), and Model WIN-PS-5CC-R (five-output plug-in power module).

        - Configurable power supply panels with up to 10 or 30 outputs (using required number of plug-in power modules) for shades, keypads and accessories, and for providing additional low voltage power to communication link; no replaceable fuses required for overload/miswire protection.

          - 10-output configurable smart enclosure

          - 30-output configurable smart enclosure.

          - Plug-in Power Module:  Five output; DOE Level VI Compliant.

The following is based on Lutron Model QSPS-10PNL.

        - Ten output power supply panel for shades, keypads and accessories, and for providing additional low voltage power to communication link; no replaceable fuses required for overload/miswire protection; contains DOE Level VI Compliant power supplies.

The following is based on Lutron Model QSPSY-10PNL.

        - Ten output power supply panel for wireless shades, keypads and accessories, and for providing additional low voltage power to communication link; no replaceable fuses required for overload/miswire protection; contains DOE Level VI Compliant power supplies.

The following is based on Lutron Model QSPS-DH-1-75.

        - Power supply for keypads and accessories (not for shades/window treatments), and for providing additional low voltage power to communication link.

The following is based on Lutron Model WQSPS-DH-1-75.

        - Power supply for keypads and accessories (not for shades/window treatments), and for providing additional low voltage power to communication link; TAA – Trade Agreement Act compliant.

    - Provide locking covers for controls <<where indicated; located _________; or __________>>.

      - Reversible to allow lock to be located on either side of control.

      - Compatible with IR controls.

      - Does not reduce specified IR range by more than 50 percent of its original specification.

      - Product(s):

        - 1-gang device for compatible keypads.

  - SHADE FABRICATION

    - Field measure finished openings prior to ordering or fabrication.

--CHOOSE ONLY ONE OF THE TWO PARAGRAPHS BELOW—

Include the following paragraph to refer to manufacturer for tolerances or include the paragraph below to specify tolerances.

    - Dimensional Tolerances:  As recommended in writing by manufacturer.

    - Dimensional Tolerances:  Fabricate shades to fit openings within specified tolerances.

      - Vertical Dimensions - Inside Mounting: Fill openings from head to sill with <<1/2 inch (13 mm); ___ inch (___ mm)>> space between bottom bar and <<window sill; finish floor; window stool; or _______>>.

If "light gap dimension" is critical, use the following paragraph and choice box to define parameters.

      - Horizontal Dimensions - Inside Mounting: Provide symmetrical light gaps on both sides of shade not to exceed <<3/4 inch (19.05 mm); ___ inch (___ mm)>>.

      - <<Horizontal; Horizontal and Vertical; or _____>> Dimensions - Outside Mounting: Cover window frames, trim, and casings completely.

      - Horizontal Dimensions - Outside Mounting: Extend shades <<2 inches (50 mm); ___ inches (___ mm)>> beyond jambs on each side.

    - At openings requiring continuous multiple shade units with separate rollers, locate roller joints at window mullion centers; butt rollers end-to-end.

For shades that are very tall or very wide, horizontal battens can be seamed into the fabric to provide stability and ensure the best performance. Only certain fabrics are available with battens; verify with manufacturer.

    - Fabricate horizontal sealed battens into the fabric for shade stability.

Railroading rotates the fabric 90 degrees from its typical orientation. If the fabric has a distinct pattern, the final appearance will be altered. Verify options with manufacturer before specifying railroading. Only certain fabrics can be railroaded; verify with manufacturer.

    - Railroad<< and seam; or _____>> fabric for applications that are wider than the usable fabric roll width.

  - SOURCE QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - Factory Testing:

To ensure that 100 percent of the shade control products work at installation, the manufacturer should test 100 percent of all assemblies at full rated load in the factory. This testing will assure that every product has been tested and guaranteed to work. Sampling would only prove that the samples work and should not be acceptable.

      - Perform full-function factory testing on all completed assemblies. Statistical sampling is not acceptable.

- EXECUTION

  - EXAMINATION

    - Motorized Shades and Controls: Verify that ratings and configurations of system components are consistent with the indicated requirements.

    - Examine finished openings for deficiencies that may preclude satisfactory installation.

    - If substrate preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

    - Start of installation shall be considered acceptance of substrates.

  - PREPARATION

    - Prepare surfaces using methods recommended by manufacturer for achieving best result for substrate under the project conditions.

    - Coordinate with window installation and placement of concealed blocking to support shades.

  - INSTALLATION

    - Install products in accordance with manufacturer's instructions.

    - Shade Installation:

      - Install in accordance with approved shop drawings, using mounting devices as indicated.

      - Installation Tolerance: <<1/16 inch (1.5 mm); ___ inch (___ mm)>> maximum offset from level.

      - Replace shades that exceed specified dimensional tolerances at no extra cost to Owner.

      - Adjust level, projection and shade centering from mounting bracket where applicable.

      - Verify there is no telescoping of shade fabric. Ensure smooth shade operation.

Include the following paragraph only if motorized shade controls are specified in this section.

    - Motorized Shade Control Installation:

      - Perform work in a neat and workmanlike manner in accordance with NECA 1 and, where applicable, NECA 130<<, except for mounting heights specified in those standards;, including mounting heights specified in those standards unless otherwise indicated; or __________>>.

      - Adjust open and closed limits set by the manufacturer as required.

      - Assign each shade to a shade group and set control functions.

      - Identify system components in accordance with Section 26 0553.

  - FIELD QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - Manufacturer's startup services will not be required.

    - Correct defective work, adjust for proper operation, and retest until entire system complies with contract documents.

  - CLEANING

    - Clean soiled shades and exposed components as recommended by manufacturer.

    - Replace shades that cannot be cleaned to "like new" condition.

  - CLOSEOUT ACTIVITIES

    - See Section 01 7800 - Closeout Submittals, for closeout submittals.

    - See Section 01 7900 - Demonstration and Training, for additional requirements.

    - Training:

      - Shade control system installer to perform on-site training of Owner's personnel on operation, adjustment, and maintenance of shade control system.

  - PROTECTION

    - Protect installed products from subsequent construction operations.

    - Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION