SECTION 26 0924

LIGHTING CONTROLS - LUTRON VIVE

This section includes wireless lighting controls for single spaces such as classrooms, private offices, and conference rooms and features Vive®  basis of design products from Lutron Electronics Company, Inc. System components include wireless occupancy/vacancy sensors, wireless daylight sensors, wireless load control modules, wired dimmers and switches with wireless communication inputs, wireless control stations, fluorescent electronic dimming ballasts, LED drivers, power interfaces, digital dimming ballast modules and wireless hub(s) for centralized control, monitoring, and system integration.

LIGHTING CONTROLS - LUTRON VIVE, Copyright 2016-2024, Lutron Electronics Company, Inc.

- GENERAL

  - SECTION INCLUDES

    - Single space wireless lighting control systems and associated components:

      - Wireless occupancy/vacancy sensors.

      - Wireless daylight sensors.

      - Wired load control modules with wireless communication inputs.

        - Includes fixture control modules with wired occupancy/vacancy/daylight sensors.

      - Wired receptacles with wireless communication inputs.

      - Wireless fixture control components factory-installed in luminaires not specified in this section.

      - Wired wall dimmers and switches with wireless communication inputs.

      - Wired wallbox occupancy sensors with wireless communication inputs.

      - Wireless control stations.

      - LED Drivers.

      - Power interfaces.

      - Digital dimming ballast modules.

    - Wireless hub(s) for centralized control, monitoring, and system integration.

    - Software data and analytics dashboard, including server requirements.

  - RELATED REQUIREMENTS

    - Section <<______>>: Building automation system, for interface with lighting control system.

    - Section 26 0553 - Identification for Electrical Systems:  Identification products and requirements.

    - Section 26 2726 - Wiring Devices - Lutron:

      - Finish requirements for wall controls specified in this section.

      - Accessory receptacles and wallplates, to match lighting controls specified in this section.

    - Section 26 5133 - Luminaires and Drivers - Lutron.

  - REFERENCE STANDARDS

    - 47 CFR 15 - Radio Frequency Devices; current edition.

    - ANSI C82.11 - American National Standard for Lamp Ballasts - High Frequency Fluorescent Lamp Ballasts - Supplements; 2011.

    - ANSI/ESD S20.20 - Protection of Electrical and Electronic Parts, Assemblies and Equipment (Excluding Electrically Initiated Explosive Devices); 2014.

    - ASTM D4674 - Standard Practice for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Office Environments; 2002a (Reapproved 2010).

    - CAL TITLE 24 P6 – California Code of Regulations, Title 24, Part 6 (California Energy Code); 2013.

    - CSA C22.2 No. 223 – Power Supplies with Extra-low-voltage Class 2 Outputs; 2015.

    - IEC 60929 - AC and/or DC-Supplied Electronic Control Gear for Tubular Fluorescent Lamps - Performance Requirements; 2015.

    - IEC 61000-4-2 - Electromagnetic Compatibility (EMC) - Part 4-2: Testing and Measurement Techniques - Electrostatic Discharge Immunity Test; 2008.

    - IEC 61347-2-3 - Lamp Control Gear - Part 2-3: Particular Requirements for A.C. and/or D.C. Supplied Electronic Control Gear for Fluorescent Lamps; 2011, with Amendments, 2016.

    - IEEE 1789 - Recommended Practice for Modulating Current in High-Brightness LEDs for Mitigating Health Risks to Viewers; 2015.

    - IEEE C62.41.2 - Recommended Practice on Characterization of Surges in Low-Voltage (1000 V and less) AC Power Circuits; 2002 (Cor 1, 2012).

    - ISO 9001 - Quality Management Systems-Requirements; 2008.

    - NECA 1 - Standard for Good Workmanship in Electrical Construction; 2015.

    - NECA 130 - Standard for Installing and Maintaining Wiring Devices; National Electrical Contractors Association; 2010.

    - NEMA 410 - Performance Testing for Lighting Controls and Switching Devices with Electronic Drivers and Discharge Ballasts; National Electrical Manufacturers Association; 2015.

    - NEMA SSL 7A – Phase Cut Dimming for Solid State Lighting:  Basic Compatibility; National Electrical Manufacturers Association; 2015.

    - NEMA WD 1 - General Color Requirements for Wiring Devices; National Electrical Manufacturers Association; 1999 (R 2015).

    - NFPA 70 - National Electrical Code; National Fire Protection Association; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.

    - UL 20 - General-Use Snap Switches; Current Edition, Including All Revisions.

    - UL 508 - Industrial Control Equipment; Underwriters Laboratories Inc.; Current Edition, Including All Revisions.

    - UL 924 – Emergency Lighting and Power Equipment; Current Edition, Including All Revisions.

    - Lighting and Power Equipment; Current Edition, Including All Revisions.

    - UL 1310 – Class 2 Power Units; Current Edition, Including All Revisions.

    - UL 1472 - Solid-State Dimming Controls; Current Edition, Including All Revisions.

    - UL 1598C - Light-Emitting Diode (LED) Retrofit Luminaire Conversion Kits; Current Edition, Including All Revisions.

    - UL 2043 - Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces; Current Edition, Including All Revisions.

    - UL 8750 - Light Emitting Diode (LED) Equipment for Use in Lighting Products; Current Edition, Including All Revisions.

  - ADMINISTRATIVE REQUIREMENTS

    - Coordination:

      - Coordinate the placement of sensors and wall controls with millwork, furniture, equipment, etc. installed under other sections or by others.

      - Coordinate the placement of wall controls with actual installed door swings.

      - Coordinate the placement of daylight sensors with windows, skylights, and luminaires to achieve optimum operation. Coordinate placement with ductwork, piping, equipment, or other potential obstructions to light level measurement installed under other sections or by others.

      - Coordinate the work to provide luminaires and lamps compatible with the lighting controls to be installed.

      - Notify Architect of any conflicts or deviations from the contract documents to obtain direction prior to proceeding with work.

    - Pre-Wire Meeting:  Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to conduct on-site meeting prior to commencing work. Manufacturer to review with installer:

      - Low voltage wiring requirements.

      - Separation of power and low voltage/data wiring.

      - Wire labeling.

      - Wireless hub locations and installation.

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS".

      - Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS", sensor locations to be reviewed in accordance with layout provided by Lighting Control Manufacturer. Lighting Control Manufacturer may direct Contractor regarding sensor relocation should conditions require a deviation from locations indicated.

      - Control locations.

      - Computer jack locations.

      - Load circuit wiring.

      - Network wiring requirements.

      - Connections to other equipment.

      - Installer responsibilities.

    - Sequencing:

      - Do not install sensors and wall controls until final surface finishes<< and painting>> are complete.

  - SUBMITTALS

    - See Section 01 3000 - Administrative Requirements for submittal procedures.

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS".

    - Design Documents: Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS", Lighting Control Manufacturer to provide plans indicating occupancy/vacancy and/or daylight sensor locations.

    - Product Data: Include ratings, configurations, standard wiring diagrams, dimensions, colors, service condition requirements, and installed features.

      - Occupancy/Vacancy Sensors: Include detailed basic motion detection coverage range diagrams.

      - Wall Dimmers: Include derating information for ganged multiple devices.

    - Samples:

      - Wall Controls:

        - Show available color and finish selections.

        - Provide <<one; or _____>> sample(s) for each product<< proposed for substitution; or __________>><< upon request; or __________>>.

      - Sensors: Provide <<one; or _____>> sample(s) for each product<< proposed for substitution; or __________>><< upon request; or __________>>.

    - Manufacturer's Installation Instructions: Include application conditions and limitations of use stipulated by product testing agency. Include instructions for storage, handling, protection, examination, preparation, and installation of product.

Use the following paragraph to specify system performance-verification documentation at an additional cost (requires On-Site Full-Scope Start-Up Service to be specified under ‘FIELD QUALITY CONTROL” in Part 3). System Performance-Verification Documentation is often required for LEED projects, projects which involve a commissioning agent, or Title 24 (California) projects. Edit the second choice to have this additional cost included as an alternate or as part of the base bid.

This documentation will be completed by a Lutron Services Company Representative during the startup of the Lutron lighting control system. This documentation defines the functional test procedures to be used and the results of the onsite testing of the Lutron equipment. A copy of this documentation will be delivered after startup completion.

    - System Performance-Verification Documentation: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's enhanced documentation detailing start-up performance-verification procedures and functional tests performed along with test results.

Include the following paragraph if lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) is specified in Part 3 under "COMMISSIONING".

    - Title 24 Acceptance Testing Documentation:  Submit Certification of Acceptance and associated documentation for lighting control acceptance testing performed in accordance with CAL TITLE 24 P6, as specified in Part 3 under “COMMISSIONING”.

    - Project Record Documents: Record actual installed locations and settings for lighting control system components.

    - Operation and Maintenance Data: Include detailed information on lighting control system operation, equipment programming and setup, replacement parts, and recommended maintenance procedures and intervals.

    - Warranty: Submit sample of manufacturer's Warranty or Enhanced Warranty as specified in Part 1 under “WARRANTY”. Submit documentation of final executed warranty completed in Owner's name and registered with manufacturer.

  - QUALITY ASSURANCE

    - Conform to requirements of NFPA 70.

    - Maintain at the project site a copy of each referenced document that prescribes execution requirements.

    - Manufacturer Qualifications:

With the proliferation of wireless devices, experience working with RF controls is critical to understanding good design for reliability.

      - Company with not less than ten years of experience manufacturing lighting control products using wireless communication between devices.

      - Registered to ISO 9001, including in-house engineering for product design activities.

If there is a problem on the job site, the manufacturer must be reachable 24 hours per day, 7 days per week to resolve any lighting control issues. If this service is not provided, project cost overruns and delays can occur. Additionally, answering services can add to frustration and delays.

      - Provides factory direct technical support hotline available 24 hours per day, 7 days per week.

      - Qualified to supply specified products and to honor claims against product presented in accordance with warranty.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in a clean, dry space in original manufacturer's packaging in accordance with manufacturer's written instructions until ready for installation.

  - FIELD CONDITIONS

    - Maintain field conditions within manufacturer's required service conditions during and after installation.

      - Basis of Design System Requirements, Unless Otherwise Indicated:

        - Ambient Temperature:

          - Lighting Control System Components: Between 32 and 104 degrees F (0 and 40 degrees C).

        - Relative Humidity: Less than 90 percent, non-condensing.

        - Protect lighting controls from dust.

  - WARRANTY

    - See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

--CHOOSE ONLY ONE OF THE TWO STANDARD WARRANTIES BELOW ACCORDING TO WHETHER OR NOT MANUFACTURER FULL-SCOPE START-UP SERVICES WILL BE SPECIFIED IN PART 3--

Use the following paragraph if there will be no Manufacturer Full-Scope Start-Up, or use the standard warranty paragraph below if Lutron Full-Scope Start-Up Service will be specified in Part 3 under "FIELD QUALITY CONTROL". Keep in mind however that without Lutron Start-up service, Standard Warranty coverage is significantly reduced.

    - Manufacturer's Standard Warranty, Without Manufacturer Full-Scope Start-Up:

      - Manufacturer Lighting Control System Components, Except Wireless Sensors, Drivers and Load Control Modules: One year 100 percent parts coverage, no manufacturer labor coverage.

      - Wireless Sensors:  Five years 100 percent parts coverage, no manufacturer labor coverage.

      - Drivers and Load Control Modules: Three years 100 percent parts coverage, no manufacturer labor coverage.

Use the following paragraph if Lutron Full-Scope Start-Up Service will be specified in Part 3 under "FIELD QUALITY CONTROL", or use the standard warranty paragraph above if there will be no Manufacturer Full-Scope Start-Up. Keep in mind however that without Lutron Start-Up Service, Standard Warranty coverage is significantly reduced.

Lutron Standard 2-Year Warranty coverage includes:

-100 percent parts and labor coverage for first two years for lighting control system components, except ballasts/drivers and ballast modules.

-First-available on-site or remote response time.

-Telephone technical support; 24 hours per day, 7 days per week, excluding manufacturer holidays.

Consider including an optional Enhanced Warranty below (at an additional cost).

    - Manufacturer's Standard Warranty, With Manufacturer Full-Scope Start-Up:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Drivers and Load Control Modules:

        - First Two Years:

          - 100 percent replacement parts coverage, 100 percent manufacturer labor coverage to troubleshoot and diagnose a lighting issue.

          - First-available on-site or remote response time.

          - Remote diagnostics for applicable systems.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

      - Lighting Management System Computer: One year 100 percent parts coverage, one year 100 percent manufacturer labor coverage.

      - Drivers and Load Control Modules:

Include the following paragraph only if Lutron Remote Full-Scope Start-Up Service is specified in Part 3 under "FIELD QUALITY CONTROL".

        - With Remote Full-Scope Start-Up: Three years 100 percent parts coverage, no manufacturer labor coverage.

        - With On-Site Full-Scope Start-Up: Five years 100 percent parts coverage, no manufacturer labor coverage.

Use one of the following three paragraphs to specify an optional Enhanced Warranty. Edit the choice to have this additional value included as an alternate or as part of the base bid.

If an Enhanced Warranty is specified without specifying Lutron On-Site Full-Scope Start-Up Service in Part 3 under “FIELD QUALITY CONTROL”, a Warranty Audit Visit must be specified in Part 3 under “CLOSEOUT ACTIVITIES”. Also keep in mind that without Lutron Start-Up Service, Standard Warranty coverage is significantly reduced. Visit www.lutron.com for warranty information.

Lutron Silver Enhanced Warranty (LSC-E8S) includes standard 2-year warranty coverage plus:

-Upgrade to 8-year limited parts warranty coverage for lighting control system components, excluding ballasts/drivers and ballast modules.

Lutron Gold Enhanced Warranty (LSC-E8G) includes standard 2-year warranty coverage plus:

-Upgrade to 8-year limited parts warranty coverage for lighting control system components, excluding ballasts/drivers and ballast modules.

-Upgrade to 72-hour on-site response time.

-Annual scheduled Preventative Maintenance Visit.

Lutron Platinum Enhanced Warranty (LSC-E8P) includes standard 2-year warranty coverage plus:

-Upgrade to 8-year limited parts warranty coverage for lighting control system components, excluding ballasts/drivers and ballast modules.

-Upgrade to 24-hour on-site response time.

-Annual scheduled Preventative Maintenance Visit.

--CHOOSE ONLY ONE OF THE THREE OPTIONAL ENHANCED WARRANTIES BELOW—

The following is based on Lutron Silver Enhanced Warranty.

    - Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's enhanced warranty:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Drivers and Load Control Modules:

        - First Two Years:

          - 100 percent replacement parts coverage, 100 percent manufacturer labor coverage to troubleshoot and diagnose a lighting issue.

          - Remote diagnostics for applicable systems.

          - As-available Field Service response; no committed response time.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

      - Lighting Management System Computer: One year 100 percent parts coverage, one year 100 percent manufacturer labor coverage.

      - Drivers and Load Control Modules:

        - With Remote Full-Scope Start-Up or no Full-Scope Start-Up: Three years 100 percent parts coverage, no manufacturer labor coverage.

        - With On-Site Full-Scope Start-Up: Five years 100 percent parts coverage, no manufacturer labor coverage.

The following is based on Lutron Gold Enhanced Warranty.

    - Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's enhanced warranty:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Drivers and Load Control Modules:

        - First Two Years:

          - 100 percent replacement parts coverage, 100 percent manufacturer labor coverage to troubleshoot and diagnose a lighting issue.

          - Remote diagnostics for applicable systems.

          - Upgrade from as-available Field Service to 72-hour on-site or remote response time.

          - Plus annual scheduled Preventive Maintenance Visit.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

      - Lighting Management System Computer: One year 100 percent parts coverage, one year 100 percent manufacturer labor coverage.

      - Drivers and Load Control Modules:

        - With Remote Full-Scope Start-Up or no Full-Scope Start-Up: Three years 100 percent parts coverage, no manufacturer labor coverage.

        - With On-Site Full-Scope Start-Up: Five years 100 percent parts coverage, no manufacturer labor coverage.

The following is based on Lutron Platinum Enhanced Warranty.

    - Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's enhanced warranty:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Drivers and Load Control Modules:

        - First Two Years:

          - 100 percent replacement parts coverage, 100 percent manufacturer labor coverage to troubleshoot and diagnose a lighting issue.

          - Remote diagnostics for applicable systems.

          - Upgrade from as-available Field Service to 24-hour on-site or remote response time.

          - Plus annual scheduled Preventive Maintenance Visit.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

      - Lighting Management System Computer: One year 100 percent parts coverage, one year 100 percent manufacturer labor coverage.

      - Drivers and Load Control Modules:

        - With Remote Full-Scope Start-Up or no Full-Scope Start-Up: Three years 100 percent parts coverage, no manufacturer labor coverage.

        - With On-Site Full-Scope Start-Up: Five years 100 percent parts coverage, no manufacturer labor coverage.

- PRODUCTS

  - MANUFACTURERS

    - Basis of Design Manufacturer: Lutron Electronics Company, Inc; Vive; www.lutron.com.

    - Other Acceptable Manufacturers:

      - <<__________>>.

      - <<__________>>.

      - Products by listed manufacturers are subject to compliance with specified requirements<< and prior approval of Architect or _________>>.

    - Substitutions: <<See Section 01 6000 - Product Requirements; Not permitted; or __________>>.

      - All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by Architect a minimum of <<10; or _____>> working days prior to the bid date and must be made available to all bidders. Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

      - Any proposed substitutions to be reviewed by Architect at Contractor's expense<< at a rate of $200 per hour; at a rate of _________; or __________>>.

      - By using pre-approved substitutions, Contractor accepts responsibility and associated costs for all required modifications to related equipment and wiring. Provide complete engineered shop drawings (including power wiring) with deviations from the original design highlighted in an alternate color for review and approval by Architect prior to rough-in.

    - Source Limitations: Furnish products produced by a single manufacturer and obtained from a single supplier.

  - LIGHTING CONTROLS - GENERAL REQUIREMENTS

Use the following paragraph to specify optional manufacturer Sensor Layout and Tuning (requires On-Site Full-Scope Start-Up Service to be specified under “FIELD QUALITY CONTROL” in Part 3 and Pre-Wire Meeting to be specified under “ADMINISTRATIVE REQUIREMENTS” in Part 1). Edit the choice to have this additional value included as an alternate or as part of the base bid.

    - Sensor Layout and Tuning: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer's Sensor Layout and Tuning service:

      - Lighting Control Manufacturer to take full responsibility for wired or wireless occupancy/vacancy and daylight sensor layout and performance for sensors provided by Lighting Control Manufacturer.

      - Lighting Control Manufacturer to analyze the reflected ceiling plans, via supplied electronic AutoCAD format, and design a detailed sensor layout that provides adequate occupancy sensor coverage and ensures occupancy and daylight sensor performance per agreed upon sequence of operations. Contractor to utilize the layouts for sensor placement.

      - During startup, Lighting Control Manufacturer to direct Contractor regarding sensor relocation, as required, should conditions require a deviation from locations specified in the drawings.

      - Lighting Control Manufacturer to provide up to two additional post-startup on-site service visits, within one calendar year from Date of Substantial Completion to fine-tune sensor calibration per the agreed upon sequence of operations.

    - Provide products listed, classified, and labeled by Underwriter's Laboratories Inc. (UL) as suitable for the purpose indicated.

    - Unless specifically indicated to be excluded, provide all required equipment, conduit, boxes, wiring, connectors, hardware, supports, accessories, programming, etc. as necessary for a complete operating system that provides the control intent indicated.

Typical dimming equipment is rated for 40 degrees C (104 degrees F). This is the maximum ambient temperature that can exist while the dimming equipment is operating at full load conditions. Include the following paragraph to ensure that the operating equipment is designed to operate at worst case environmental conditions without affecting product life.

    - Design lighting control equipment for 10 year operational life while operating continually at any temperature in an ambient temperature range of 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C) and 90 percent non-condensing relative humidity.

    - Electrostatic Discharge Tolerance: Design and test equipment to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

Power dropouts occur frequently. The momentary interruption of power should not cause extended periods without lighting or require some manual intervention to reset the lighting system. Some manufacturers may define power failure memory as a feature that handles momentary power outages on the order of 20 seconds. This does not account for power outages that occur for a longer period of time.

    - Power Failure Recovery: When power is interrupted for periods up to <<10 years; or __________>> and subsequently restored, lights to automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

    - Wireless Devices:

      - Wireless device family includes area or fixture level sensors, area or fixture level load controls for dimming or switching, and load controls that can be mounted in a wallbox, on a junction box, or at the fixture.

      - Wireless devices including sensors, load controls, and wireless remotes or wall stations, can be set up using simple button press programming without needing any other equipment (e.g. central hub, processor, computer, or other smart device).

      - Wireless hub adds the ability to set up the system using any smart device with a web browser (e.g. smartphone, tablet, PC, or laptop).

      - System does not require a factory technician to set up or program the system.

      - Capable of diagnosing system communications.

      - Capable of having addresses automatically assigned to them.

      - Receives signals from other wireless devices and provides feedback to user.

      - Capable of determining which devices have been addressed.

      - RF Range: 60 feet (18 m) line-of-sight or 30 feet (9 m) through typical construction materials between RF transmitting devices and compatible RF receiving devices.

The FCC sets limits on EMI/RFI for both non-consumer (commercial and industrial) and consumer (residential) applications. The class B, consumer limits are more stringent than the class A, non-consumer limits.

      - Electromagnetic Interference/Radio Frequency Interference (EMI/RFI) Limits: Comply with FCC requirements of CFR, Title 47, Part 15, for Class B application.

    - Wireless Network:

      - RF Frequency: 434 MHz; operate in FCC governed frequency spectrum for periodic operation; continuous transmission spectrum is not permitted.

        - Wireless sensors, wireless wall stations and wireless load control devices do not operate in the noisy 2.4 GHz frequency band where high potential for RF interference exists.

        - Wireless devices operate in an uncongested frequency band providing reliable operation.

        - Fixed network architecture ensures all associated lights and load controls respond in a simultaneous and coordinated fashion from a button press, sensor signal, or command from the wireless hub (i.e. no popcorning).

      - Distributed Architecture:  Local room devices communicate directly with each other. If the wireless hub is removed or damaged, local control, sensing, and operation continues to function without interruption.

      - Local room devices communicate directly with each other (and not through a central hub or processor) to ensure:

        - Reliability of system performance.

        - Fast response time to events in the space (e.g. button presses or sensor signals).

        - Independent operation in the event of the wireless hub being removed or damaged.

    - Device Finishes:

--CHOOSE ONE OF THE TWO PARAGRAPHS BELOW--

      - Wall Controls:  Match finishes for Wiring Devices in Section 26 2726, unless otherwise indicated.

      - Wall Controls: <<As indicated on the drawings; White; Black; Ivory; Light Almond; To be selected by Architect; or __________>>.

      - Standard Colors: Comply with NEMA WD1 where applicable.

      - Color Variation in Same Product Family: Maximum delta E of 1, CIE L*a*b color units.

Daylight or fluorescent lighting generate ultraviolet light which can cause parts that do not meet ASTM D4674 to discolor/yellow over time.

      - Visible Parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

Use the following paragraph if interface with building automation system will be required. Any specific requirements can be added as subparagraphs below.

    - Interface with building automation system<< as specified in Section _____>>.

  - WIRELESS SENSORS

    - General Requirements:

      - Operational life of 10 years without the need to replace batteries when installed per manufacturer's instructions.

      - Communicates directly to compatible RF receiving devices through use of a radio frequency communications link.

      - Does not require external power packs, power wiring, or communication wiring.

      - Capable of being placed in test mode to verify correct operation from the face of the unit.

The following products are based on Lutron Radio Powr Savr Series.

Lutron's occupancy/vacancy sensors are wireless, battery-powered passive infrared (PIR) sensors that automatically control lights via RF communication to compatible dimming and switching devices. These sensors detect the heat from people moving within an area to determine when the space is occupied. The sensors then wirelessly transmit the appropriate commands to the associated dimming and switching devices to turn the lights on or off automatically. They combine both convenience and exceptional energy savings along with ease of installation.

    - Wireless Occupancy/Vacancy Sensors:

      - General Requirements:

        - Provides a clearly visible method of indication to verify that motion is being detected during testing and that the unit is communicating to compatible RF receiving devices.

Include the following paragraph to ensure that the line-of-sight is not obstructed due to dust and other contaminants.

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Lutron's XCT signal processing technology greatly enhances the performance of PIR sensors, enabling them to "see" fine motions that other sensors couldn't previously detect. Plus, the user-replaceable batteries are designed to last up to 10 years.

        - Sensing Mechanism: Passive infrared coupled with technology for sensing fine motions. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor's sensitivity threshold.

        - Provide optional, readily accessible, user-adjustable controls for timeout, automatic/manual-on, and sensitivity.

        - Turns off lighting after reasonable and adjustable time delay once the last person to occupy the space vacates a room or area. Provide adjustable timeout settings of 1, 5, 15, and 30 minutes.

        - Capable of turning dimmer's lighting load on to an optional locked preset level selectable by the user. Locked preset range to be selectable on the dimmer from 1 percent to 100 percent.

        - Color: White.

        - Provide all necessary mounting hardware and instructions for both temporary and permanent mounting.

        - Provide temporary mounting means for drop ceilings to allow user to check proper performance and relocate as needed before permanently mounting sensor. Temporary mounting method to be design for easy, damage-free removal.

        - Sensor lens to illuminate during test mode when motion is detected to allow installer to place sensor in ideal location and to verify coverage prior to permanent mounting.

        - Ceiling-Mounted Sensors:

          - Provide surface mounting bracket compatible with drywall, plaster, wood, concrete, and compressed fiber ceilings.

          - Provide recessed mounting bracket compatible with drywall and compressed fiber ceilings.

        - Wall-Mounted Sensors: Provide wall or corner mounting brackets compatible with drywall and plaster walls.

      - Wireless Combination Occupancy/Vacancy Sensors:

-Wireless occupancy sensor has three settings available: Auto-On/Auto-Off, Auto-On Low-Light/Auto-Off, and Manual-On/Auto-Off

-Auto-On Low-Light feature will only turn lights on automatically if there is less than approximately 1 fc (10 lux) of ambient light

-Simple and intuitive adjustments available for Timeout, Auto-On, and Activity settings

-Supports advanced occupancy features, such as dependent occupancy groups and customizable occupied/unoccupied presets in some systems

-Refer to product specification submittal of receiving device to determine system limits.

        - Ceiling-Mounted Sensors: Programmable to operate as an occupancy sensor (automatic-on and automatic-off), an occupancy sensor with low light feature (automatic-on when less than one footcandle of ambient light available and automatic-off), or a vacancy sensor (manual-on and automatic-off).

-Wireless occupancy sensor has two settings available: Auto-On/Auto-Off, and Manual-On/Auto-Off

-Simple and intuitive adjustments available for Timeout, Activity, and Auto-On settings

-Supports advanced occupancy features, such as dependent occupancy groups and customizable occupied/unoccupied presets in some systems

-Refer to product specification submittal of receiving device to determine system limits

        - Wall-Mounted Sensors: Programmable to operate as an occupancy sensor (automatic-on and automatic-off), or a vacancy sensor (manual-on and automatic-off).

The following products are based on Lutron Radio Powr Savr Series.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

Wireless ceiling-mounted occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology for sensing fine motion. Sensor can be auto-on/auto-off, auto-on low light/auto-off, or manual on/auto-off. Ceiling-mounted sensors are recommended for spaces with ceilings less than 12 feet high.

          - <<Type _____ - >>Ceiling-Mounted Occupancy/Vacancy Sensor: Coverage from 324 square feet (30.2 sq m) to 676 square feet (62.4 sq m) depending on ceiling height from 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

Wireless 180 degree coverage wall-mount occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Wall-Mounted Occupancy/Vacancy Sensor: Minor motion coverage of 1500 square feet (139.4 sq m) and major motion coverage of 3000 square feet (278.7 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 180 degree field of view.

Wireless 90 degree coverage corner-mount occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Corner-Mounted Occupancy/Vacancy Sensor: Minor motion coverage of 1225 square feet (113.8 sq m) and major motion coverage of 2500 square feet (232.3 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 90 degree field of view.

Wireless hallway occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Hallway Occupancy/Vacancy Sensor: Major motion coverage of up to 150 feet (45.7 m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); narrow field of view.

      - Wireless Vacancy-Only Sensors:

Visit www.lutron.com for more information on California Title 24 requirements.

        - Operates only as a vacancy sensor (manual-on and automatic-off)<< in accordance with CAL TITLE 24 P6 24 requirements>>.

The following products are based on Lutron Radio Powr Savr Series.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

Wireless ceiling-mounted vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology for sensing fine motion. Sensor is manual on/auto-off (meets California Title 24 requirements). Ceiling-mounted sensors are recommended for spaces with ceilings less than 12 feet high.

          - <<Type _____ - >>Ceiling-Mounted Vacancy-Only Sensor: Coverage from 324 square feet (30.2 sq m) to 676 square feet (62.4 sq m) depending on ceiling height from 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

Wireless 180 degree coverage wall-mount vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Wall-Mounted Vacancy-Only Sensor: Minor motion coverage of 1500 square feet (139.4 sq m) and major motion coverage of 3000 square feet (278.7 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 180 degree field of view.

Wireless 90 degree coverage corner-mount vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Corner-Mounted Vacancy-Only Sensor: Minor motion coverage of 1225 square feet (113.8 sq m) and major motion coverage of 2500 square feet (232.3 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 90 degree field of view.

Wireless hallway vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Hallway Vacancy-Only Sensor: Major motion coverage of up to 150 feet (45.7 m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); narrow field of view.

The following products are based on Lutron Radio Powr Savr Series.

    - Wireless Daylight Sensors:

Lutron's wireless daylight sensor is a battery-powered sensor that automatically controls lights via RF communication to compatible dimming or switching devices. This sensor mounts to the ceiling and measures light in the space. The sensor then wirelessly transmits the light level to the associated dimming or switching devices that automatically control the lights to balance light level in the space. The sensor combines both convenience and exceptional energy savings along with ease of installation.

      - Open-loop basis for daylight sensor control scheme.

      - Stable output over temperature from 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C).

      - Partially shielded for accurate detection of available daylight to prevent fixture lighting and horizontal light component from skewing sensor detection.

      - Provide linear response from 2 to 150 footcandles.

      - Color: White.

      - Mounting:

        - Provide surface mounting bracket compatible with drywall, plaster, wood, concrete, and compressed fiber ceilings.

        - Provide all necessary mounting hardware and instructions for both temporary and permanent mounting.

        - Provide temporary mounting means for drop ceilings to allow user to check proper performance and relocate as needed before permanently mounting sensor. Temporary mounting method to be design for easy, damage-free removal.

Visit www.lutron.com for more information on California Title 24 requirements.

      - Meets CAL TITLE 24 P6 requirements.

  - LOAD CONTROL MODULES

    - Provide wireless load control modules as indicated or as required to control the loads as indicated.

    - Junction Box-Mounted Modules:

      - Plenum rated.

Lutron's PowPak® dimming module with 0-10 V control is a radio frequency (RF) control that operates 0-10 V controlled fluorescent ballasts or LED drivers based on input from Pico® wireless controls and Radio Powr Savr™ wireless occupancy/vacancy sensors and wireless daylight sensors. The Dimming Module with 0-10 V Control is ideal for small areas (e.g., classrooms, conference rooms, private offices). Communication with RF input devices (e.g. Pico® wireless controls, Radio Powr Savr™ sensors) is accomplished by using Lutron Clear Connect® RF Technology. Visit www.lutron.com for data sheets and other information.

      - 0-10 V Dimming Modules:

        - Product(s):

          - 8 A dimming module with 0-10V control, without emergency mode.

          - 8 A dimming module with 0-10V control, with emergency mode.

        - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

IEC 60929 is a standard for electronic fluorescent ballasts, and is used by other lighting equipment controlled by low voltage signals including LED drivers and low voltage controlled neon. It defines specific methods for 0-10V, pulse width modulation (PWM), and Digitally Addressable Lighting Interface (DALI).

        - Single low voltage dimming module with Class 1 or Class 2 isolated 0-10V output signal conforming to IEC 60929 Annex E.2; source or sink automatically configures.

Certain applications, such as hallways, may require that the lights never turn off. For these areas, select the minimum light level option and the load will lower to programmed low-end level. Default operation lowers to OFF.

        - Selectable minimum light level.

        - Configurable high- and low-end trim.

        - Relay: Rated for 0-10 V ballasts, LED drivers, or fixtures that conform with NEMA 410.

        - Dimming Modules with Emergency Mode:

          - Operation With Wireless Hub:  Upon loss of power, dimming module enters and remains in emergency mode as long as wireless hub is de-energized; upon restoration of power to wireless hub, dimming module returns to normal mode and lights automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

          - Operation Without Wireless Hub:  Upon loss of power, dimming module enters and remains in emergency mode for 90 minutes, during which time local unit buttons and wireless controls are disabled.

          - Used with emergency lighting interface to achieve total system UL 924 listing.

Lutron's Vive Phase Select PowPak® dimming module is a radio frequency (RF) control that operates phase control fluorescent ballasts or LED drivers based on input from Pico® remote controls and Radio Powr Savr™ sensors. The dimming module is ideal for small areas (e.g., classrooms, conference rooms, private offices). Communication with RF input devices (e.g. Pico® remote controls, Radio Powr Savr™ sensors) is accomplished by using Lutron Clear Connect® RF Technology. Visit www.lutron.com for data sheets and other information.

      - Phase Selectable Dimming Modules:

        - Product(s):

          - Phase selectable dimming module, without emergency mode.

          - Phase selectable dimming module, with emergency mode.

        - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

        - Dimming:

          - UL listed for LED control in forward or reverse phase modes. Provide published LED performance testing on both forward and reverse phase dimming.

          - UL listed for fluorescent, electronic low voltage, and magnetic low voltage control.

        - Provides leading-edge or trailing-edge dimming; manual configuration.

Certain applications, such as hallways, may require that the lights never turn off. For these areas, select the minimum light level option and the load will lower to programmed low-end level. Default operation lowers to OFF.

        - Selectable minimum light level.

        - Configurable high- and low-end trim.

        - Provide cycle-by-cycle compensation for incoming variations, including changes in frequency, harmonics, and line noise; accommodate up to plus/minus two percent change in frequency per second.

        - Comply with NEMA SSL 7A.

        - Rated Load: Electronic low voltage (reverse phase, 450 W, 120/277 V), dimmable LED (reverse phase, 450 VA, 120/277 V; forward phase, 200 W, 120 V), incandescent/halogen (450 W, 120/277 V), magnetic low voltage (400 VA/320 W, 120/277 V) LED Driver (3 A, 120 V - maximum of 13 drivers), fluorescent (forward phase, 400 VA, 120/277 V).

        - Dimming Modules with Emergency Mode:

          - Operation With Wireless Hub:  Upon loss of power, dimming module enters and remains in emergency mode as long as wireless hub is de-energized; upon restoration of power to wireless hub, dimming module returns to normal mode and lights automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

          - Operation Without Wireless Hub:  Upon loss of power, dimming module enters and remains in emergency mode for 90 minutes, during which time local unit buttons and wireless controls are disabled.

          - Used with emergency lighting interface to achieve total system UL 924 listing.

The PowPak Single Zone Control Module with EcoSystem is a radio frequency (RF) control that operates up to 32 EcoSystem LED drivers or fluorescent ballasts for the purpose of high performance dimming and control in a Vive system or with Vive standalone products. This control is based on input from Pico remote controls and Radio Powr Savr sensors. The control module is ideal for small areas (e.g., classrooms, conference rooms, private offices). Communication with RF input devices (e.g., Pico remote controls, Radio Powr Savr sensors) is accomplished by using Lutron Clear Connect RF technology.

      - Digital Ballast/LED Driver Dimming Modules:

        - Single dimming module with Class 1 or Class 2 isolated digital output signal conforming to IEC 60929; capable of direct control without interface.

        - Provides direct low-voltage control of up to 32 compatible digital ballasts/LED drivers as a single zone (multiple ballasts/LED drivers connected to same module will be at same light level).

          - Electronically links a digital ballast/LED driver to a zone for both dimming and turning on/off.

          - Electronically assigns occupancy/vacancy sensors for manual on/auto off and auto on/auto off control.

          - Electronically assigns wireless control stations for manual local control.

          - Electronically assigns daylight sensor for automatic daylight dimming.

        - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

        - Selectable minimum light level.

        - Configurable high- and low-end trim.

Lutron's PowPak® relay module with Softswitch® is a radio frequency (RF) device that uses Lutron patented Softswitch® technology to control up to 16 A of general-purpose load (16 A and 5 A models available) based on input from Pico® wireless controls and Radio Powr Savr™ wireless occupancy/vacancy sensors and wireless daylight sensors. An optional low-voltage dry contact closure output is available to communicate occupancy status to 3rd-party systems such as HVAC controllers. PowPak® modules communicate with compatible Lutron sensors using Clear Connect® RF Technology, which ensures smooth, consistent performance. Lutron's patented Softswitch® circuit eliminates relay arcing at mechanical contacts, extending relay life to an average of 1 million cycles.

      - Relay Modules:

        - Product(s):

          - 16 A relay module, without emergency mode, without contact closure output.

          - 16 A relay module, with emergency mode, without contact closure output.

          - 16 A relay module, without emergency mode, with contact closure output.

          - 5 A relay module, without emergency mode, without contact closure output.

          - 5 A relay module, without emergency mode, with contact closure output.

        - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

Lutron Softswitch circuitry prevents arcing at the relay contacts for all three load types, and extends the relay life in excess of one million cycles. Switching high inrush loads can damage relay controls over time. The arcing of these relays, depending on load, typically will limit relay life to 10,000 or 50,000 cycles.

        - Relay:

          - Rated Life of Relay: Typical of 1,000,000 cycles at fully rated 16 A for all lighting loads.

          - Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

          - Fully rated output continuous duty for inductive, capacitive, and resistive loads.

        - Contact Closure Output:

          - Single contact closure output with normally open and normally closed dry maintained contacts suitable for connection to third party equipment (e.g. building management system, HVAC system, etc.).

          - Contact Ratings: Resistive load; 1 A at 0-24 VDC, 0.5 A at 0-24 VAC.

          - Controlled by associated occupancy/vacancy sensors and wall controls.

        - Relay Modules With Emergency Mode:

          - Operation With Wireless Hub:  Upon loss of power, relay module enters and remains in emergency mode as long as wireless hub is de-energized; upon restoration of power to wireless hub, relay module returns to normal mode and lights automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

          - Operation Without Wireless Hub:  Upon loss of power, relay module enters and remains in emergency mode for 90 minutes, during which time local unit buttons and wireless controls are disabled.

          - Used with emergency lighting interface to achieve total system UL 924 listing.

The following products are based on Lutron PowPak 20 A Receptacle Module.

      - 20 A Receptacle Modules:

        - Product(s):

          - 20 A receptacle module, without contact closure output.

          - 20 A receptacle module, with contact closure output.

        - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, and ten wireless control stations.

        - Relay:

          - Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

          - Motor rating of 1 HP at 120 V, 2 HP at 277 V.

        - Contact Closure Output:

          - Single contact closure output with normally open and normally closed dry maintained contacts suitable for connection to third party equipment (e.g. building management system, HVAC system, etc.).

          - Contact Ratings: Resistive load; 1 A at 0-24 VDC, 0.5 A at 0-24 VAC.

          - Controlled by associated occupancy/vacancy sensors and wall controls.

Lutron's PowPak® CCO Module is a radio frequency (RF) device that provides a single dry contact closure output based on input from Pico® wireless controls and Radio Powr Savr™ wireless occupancy/vacancy sensors and wireless daylight sensors. It can be powered by up to 24 VAC or 24 VDC for easy connection and integration into building management, HVAC, VAV, and other third party systems. PowPak® modules communicate with compatible Lutron sensors using Clear Connect® RF Technology, which ensures smooth, consistent performance.

      - Contact Closure Output Modules:

        - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

        - Contact Closure Output:

          - Single contact closure output with normally open and normally closed dry maintained contacts suitable for connection to third party equipment (e.g. building management system, HVAC system, etc.).

          - Contact Ratings: Resistive load; 1 A at 0-24 VDC, 0.5 A at 0-24 VAC.

          - Operation affected by associated occupancy/vacancy sensors and wall controls.

      - Wired Occupancy Transmitter Modules:

        - Communicates via wired input with wired occupancy sensors.

        - Communicates via radio frequency with compatible dimming and switching devices.

        - Provides power for up to three wired occupancy sensors.

Lutron's PowPak® wireless fixture control is a radio frequency (RF) device that controls either the Lutron EcoSystem® or 0-10 V ballasts/drivers (depending on model) based on RF input from Pico® wireless controls and Radio Powr Savr™ wireless occupancy/vacancy sensors or wired inputs from the PowPak® fixture sensor. The control module mounts to a fixture or junction box. Communication with RF input devices is accomplished using Lutron Clear Connect® RF Technology, which ensures smooth, consistent performance.

    - Fixture Control Modules/Sensors:

      - Fixture Control Modules:

        - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

        - Communicates via wired input with one combination occupancy/daylight or vacancy/daylight fixture sensor.

        - Coordination between Wired and Wireless Sensors:

          - Occupancy/Vacancy Sensing:  Wired and wireless sensors work in conjunction (occupancy detected by either sensor turns lights on and vacancy detected by both sensors turns lights off).

          - Daylight Sensing:  Wireless sensor takes precedence over wired sensor.

Certain applications, such as hallways, may require that the lights never turn off. For these areas, select the minimum light level option and the load will lower to programmed low-end level. Default operation lowers to OFF.

        - Selectable minimum light level.

        - Configurable high- and low-end trim.

        - Plenum rated.

        - Mounts to fixture or junction box through ½ inch (16 mm) trade size knockout.

        - Digital Ballast/LED Driver Fixture Control Modules:

IEC 60929 is a standard for electronic fluorescent ballasts, and is used by other lighting equipment controlled by low voltage signals including LED drivers and low voltage controlled neon. It defines a specific method for digital control.

          - Product(s):

            - Digital ballast/LED driver fixture control module, without emergency mode.

            - Digital ballast/LED driver fixture control module, with emergency mode.

          - Supports reporting of energy measurement to wireless hub at accuracy of plus/minus 2 percent or 0.5 W (whichever is higher).

          - Single integral controller with Class 1 or Class 2 isolated digital output signal conforming to IEC 60929; capable of direct control without interface.

Control of digital dimming ballasts/drivers requires the ability to address, program, and assign zone and sensor control to the digital lighting loads. Doing so can be achieved directly from the integral power and control module. Direct control of 120V and/or 277V lighting usually requires a power interface that couples both power and control. With the integral digital ballast control output, no additional interfaces are required.

          - Provides direct low-voltage control of up to 3 compatible digital ballasts/LED drivers.

            - Electronically links a digital ballast/LED driver to a zone for both dimming and turning on/off.

            - Electronically assigns occupancy/vacancy sensors for manual on/auto off and auto on/auto off control.

            - Electronically assigns wireless control stations for manual local control.

            - Electronically assigns daylight sensor for automatic daylight dimming.

          - Fixture Control Modules With Emergency Mode:

            - Operation With Wireless Hub:  Upon loss of power, fixture control module enters and remains in emergency mode as long as wireless hub is de-energized; upon restoration of power to wireless hub, fixture control module returns to normal mode and lights automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

            - Operation Without Wireless Hub:  Upon loss of power, fixture control module enters and remains in emergency mode for 90 minutes, during which time local unit buttons and wireless controls are disabled.

            - Used with emergency lighting interface to achieve total system UL 924 listing.

        - 0-10 V Dimming Fixture Control Modules:

IEC 60929 is a standard for electronic fluorescent ballasts, and is used by other lighting equipment controlled by low voltage signals including LED drivers and low voltage controlled neon. It defines specific methods for 0-10V, pulse width modulation (PWM), and Digitally Addressable Lighting Interface (DALI).

          - Product(s):

            - 0-10 V dimming fixture control module, without emergency mode.

            - 0-10 V dimming fixture control module, with emergency mode.

          - Supports reporting of energy measurement to wireless hub at accuracy of plus/minus 2 percent or 0.5 W (whichever is higher).

          - Single low voltage dimming module with Class 1 or Class 2 isolated 0-10V output signal conforming to IEC 60929 Annex E.2; source or sink automatically configures.

          - Provides 0-10 V control for up to 3 ballasts/LED drivers (1 A load at 120-277 V, 6 mA max control current).

          - Rated for switching 0-10 V ballasts, LED drivers, or fixtures that conform with NEMA 410.

          - Fixture Control Modules With Emergency Mode:

            - Operation With Wireless Hub:  Upon loss of power, fixture control module enters and remains in emergency mode as long as wireless hub is de-energized; upon restoration of power to wireless hub, fixture control module returns to normal mode and lights automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

            - Operation Without Wireless Hub:  Upon loss of power, fixture control module enters and remains in emergency mode for 90 minutes, during which time local unit buttons and wireless controls are disabled.

            - Used with emergency lighting interface to achieve total system UL 924 listing.

Lutron's PowPak® fixture sensor (optional) mounts to the ceiling or to a fixture and measures light in the space (daylighting) while detecting people moving within an area to determine passive infrared occupancy. The sensor controls the lights to balance light level in the space, combining convenience, exceptional energy savings, and ease of installation. The sensor contains two wires which connect to the PowPak® wireless fixture control.

      - Wired Fixture Sensors:

        - Product(s):

          - Wired occupancy/daylight fixture sensor.

          - Wired vacancy/daylight fixture sensor.

        - Occupancy/Vacancy Sensing:

Lutron's XCT signal processing technology greatly enhances the performance of PIR sensors, enabling them to "see" fine motions that other sensors couldn't previously detect.

          - Passive infrared coupled with technology for sensing fine motions. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor's sensitivity threshold.

          - Coverage:  300 square feet (28 sq m) with mounting height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

          - Sensor Timeout:  15 minutes.

            - Sensor timeout adjustable via wireless hub when connected to compatible fixture control module.

        - Daylight Sensing:

          - Automatic calibration.

          - Provide linear response to changes in perceived light level.

            - Response adjustable via wireless hub when connected to compatible fixture control module.

          - Closed loop proportional control scheme.

          - Sensor Range:  0 to 150 footcandles (0 to 1600 lux).

        - Mounts to fixture or ceiling.

  - WIRED RECEPTACLES WITH WIRELESS COMMUNICATION INPUTS

    - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors and ten wireless control stations.

    - Relay:

      - Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

      - Rated for switching of general purpose loads.

      - Motor rating of 0.5 HP at 120 V for 15 A receptacles, and 1 HP at 120 V for 20 A receptacles.

    - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROLS - GENERAL REQUIREMENTS article above; White; Black; Light Almond; As indicated on drawings; To be selected by Architect; or _______>>.

The following products are based on Lutron Wireless Receptacles with Clear Connect Technology.

    - Product(s):

      - Half switched duplex receptacle, 15A, 125V, NEMA 5-15R.

      - Full switched duplex receptacle, 15A, 125V, NEMA 5-15R.

      - Half switched duplex receptacle, 20A, 125V, NEMA 5-15R.

      - Full switched duplex receptacle, 20A, 125V, NEMA 5-15R.

  - LUMINAIRE COMPONENTS (FACTORY-INSTALLED)

--CHOOSE ONLY ONE OF THE FOLLOWING TWO PARAGRAPHS--

    - Wireless fixture control components to be factory-installed in luminaires as specified in Section 26 5113.

    - Luminaires specified in Section <<__________>> to be provided with factory-installed wireless fixture control components as specified below <<unless otherwise indicated; where indicated; or __________>>.

The following products are based on Lutron Vive Wireless Fixture Controller.

    - Wireless Fixture Control Dongle:

      - Product(s):

        - RF only (no integral sensing capability).

        - RF with occupancy/vacancy and daylight sensing.

      - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

Certain applications, such as hallways, may require that the lights never turn off. For these areas, select the minimum light level option and the load will lower to programmed low-end level. Default operation lowers to OFF.

      - Selectable minimum light level.

      - Supports configurable high- and low-end trim.

      - Plenum rated in accordance with UL 2043.

      - Mounts to fixture through hole.

      - Wireless Fixture Control Dongle with Integral Sensing Capabilities:

        - Occupancy/Vacancy Sensing:

Lutron's XCT signal processing technology greatly enhances the performance of PIR sensors, enabling them to "see" fine motions that other sensors couldn't previously detect.

          - Passive infrared coupled with technology for sensing fine motions. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor's sensitivity threshold.

          - Coverage:  300 square feet (28 sq m) with mounting height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

          - Sensor Timeout:  15 minutes.

            - Sensor timeout adjustable via wireless hub.

        - Daylight Sensing:

          - Automatic calibration.

          - Provide linear response to changes in perceived light level.

            - Response adjustable via wireless hub.

          - Closed loop proportional control scheme.

          - Sensor Range:  0 to 150 footcandles (0 to 1600 lux).

        - Coordination between Integral and Wireless Sensors:

          - Occupancy/Vacancy Sensing:  Integral and wireless sensors work in conjunction (occupancy detected by either sensor turns lights on and vacancy detected by both sensors turns lights off).

          - Daylight Sensing:  Wireless sensor takes precedence over integral sensor.

    - Digital Bus Interface:

      - Provides power for wireless fixture control dongle and up to four LED drivers (60mA at 17-19 VDC).

      - DALI compliant.

      - UL listed.

  - WIRED WALL DIMMERS AND SWITCHES WITH WIRELESS COMMUNICATION INPUTS

    - General Requirements:

      - Provide air gap service switch to disconnect power to load for safe lamp replacement, accessible without removing faceplate.

      - Operates at the rated capacity across the full ambient temperature range including modified capacities for ganged configurations which require removal of fins.

      - Provide radio frequency interference suppression.

      - Surge Tolerance: Designed and tested to withstand surges of 6,000 V, 200 amps according to IEEE C62.41.2 without impairment to performance.

      - Dimmers: Provide full range, continuously variable control of light intensity.

      - Dimmers for Electronic Low Voltage (ELV) Transformers:

        - Provide circuitry designed to control the input of electronic (solid-state) low voltage (ELV) transformers. Do not use dimmers that utilize standard phase control.

        - Provide resettable overload protection that provides automatic shut-off when dimmer capacity is exceeded. Do not use protection methods that are non-resettable or require device to be removed from outlet box.

        - Designed to withstand a short, per UL 1472, between load hot and either neutral or ground without damage to dimmer.

      - Dimmers for Magnetic Low Voltage (MLV) Transformers:

        - Provide circuitry designed to control and provide a symmetrical AC waveform to input of magnetic low voltage transformers per UL 1472.

        - Magnetic low voltage transformers to operate below rated current or temperature.

      - Electronic Switches:

        - Listed as complying with UL 20, UL 508, and UL 1472.

The following products are based on Lutron Maestro Wireless Series.

    - Preset Smart Wall Dimmers and Switches with Wireless Communication Inputs:

      - Communicates via radio frequency with up to ten compatible occupancy/vacancy sensors, ten wireless control stations, and one daylight sensor.

      - Dimmer Control: Multi-function tap switch with small, raised rocker for dimmer adjustment.

        - Rocker raises/lowers light level, with new level becoming the current preset level.

        - Switch single tap raises lights to preset level or fades lights to off.

        - Switch double tap raises light to full on level.

        - Switch tap and hold slowly fades lights to off over period of 10 seconds.

        - LEDs adjacent to tap switch indicate light level when dimmer is on, and function as locator light when dimmer is off.

      - Switch Control: Switch single tap turns lights on/off.

      - Dimmer High End Trim:

        - Incandescent Dimmers: Minimum of 92 percent of line voltage.

        - Dimmers for Electronic Low Voltage (ELV) Transformers: Minimum of 95 percent of line voltage.

        - Dimmers for Magnetic Low Voltage Transformers: Minimum of 92 percent of line voltage.

The following products are based on Lutron Maestro Wireless Series.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here. Visit www.lutron.com for data sheets and other information.

      - Product(s) - Preset Smart Dimmers with Wireless Communication Inputs:

        - <<Type _____ - >>Preset Smart Dimmer: Incandescent/halogen (600 W, 120 V), magnetic low voltage (600 VA/450 W, 120 V), dimmable CFL/LED (150 W, 120 V); multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

        - <<Type _____ - >>Preset Smart Dimmer: Electronic low voltage (600 W, 120 V); neutral required; multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

        - <<Type _____ - >>Preset Smart Dimmer: Incandescent (600 W, 120 V), magnetic low voltage (600 VA/450 W, 120 V); neutral required; multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

        - <<Type _____ - >>Companion Dimmer: Provides multi-location capability for compatible dimmers.

The following products are based on Lutron Maestro Wireless Series.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here. Visit www.lutron.com for data sheets and other information.

      - Product(s) - Electronic Switches with Wireless Communication Inputs:

        - <<Type _____ - >>Electronic Switch: 6 A lighting/3 A fan (120 V); neutral required; multi-location capability using companion switches (up to nine companion switches may be connected); minimum load requirement.

        - <<Type _____ - >>Electronic Switch: 8 A lighting/5.8 A fan (120 V); neutral required; multi-location capability using companion switches (up to nine companion switches may be connected); minimum load requirement.

        - <<Type _____ - >>Electronic Switch: 8 A lighting/3 A fan (120 V); 8 A lighting (277 V); multi-location capability using companion switches (up to nine companion switches may be connected); minimum load requirement.

        - <<Type _____ - >>Companion Switch: Provides multi-location capability for compatible electronic switches.

  - WIRED WALLBOX OCCUPANCY SENSORS WITH WIRELESS COMMUNICATION INPUTS

    - 0-10 V Wall Dimmer/Switch Combination Occupancy/Vacancy Sensors with Wireless Communication Inputs:

      - Communicates via radio frequency with up to ten compatible wireless occupancy/vacancy sensors, ten wireless control stations, and one wireless daylight sensor.

      - Compatible with sourcing electronic 0-10 V ballasts/drivers, as per IEC 60929 Annex E.2 0-10 V protocol.

      - Selectable option to enable low light feature (automatic-on when ambient light is below threshold). Ambient light threshold to be selectable as either adaptive utilizing occupant feedback or as fixed (high, medium, low, and minimum presets).

      - Occupancy/Vacancy Sensors:

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Lutron's XCT signal processing technology greatly enhances the performance of PIR sensors, enabling them to "see" fine motions that other sensors couldn't previously detect. Plus, the user-replaceable batteries are designed to last up to 10 years.

        - Sensing Mechanism: Passive infrared coupled with technology for sensing fine motions. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor's sensitivity threshold.

        - Programmable to operate as an occupancy sensor (automatic-on and automatic-off) or a vacancy sensor (manual-on and automatic-off).

        - Turns off lighting after reasonable and adjustable time delay once the last person to occupy the space vacates a room or area; adjustable timeout settings (1, 5, 15, or 30 minutes).

        - Adjustable sensitivity (high, medium, low, and minimum presets).

        - Selectable option to inhibit automatic turn-on of lights after manual-off operation while room is occupied for applications such as presentation viewing in conference rooms and classrooms; when room is vacated, returns to normal automatic-on operation after time delay period.

        - Selectable walk-through mode to override selected timeout and automatically turn off lights if no motion is detected within 3 minutes after initial occupancy for applications where space may be briefly occupied.

      - Vacancy-Only Sensors:

Visit www.lutron.com for more information on California Title 24 requirements.

        - Operates only as a vacancy sensor (manual-on and automatic-off)<< in accordance with California Title 24 requirements>>.

        - Adjustable sensitivity (high, medium, low, and minimum presets).

      - Dimmer Features:

        - Adjustable high/low end trims.

        - Selectable dimming curve (linear or switched).

        - Selectable fade on/fade off times (15, 5, 2.5, or 0.75 sec).

        - Adjustable auto-on light level (fully adjustable from one to 100 percent).

      - Dimmer Control: Multi-function tap switch with small, raised rocker for dimmer adjustment.

        - Rocker raises/lowers light level, with new level becoming the current preset level.

        - Switch single tap raises lights to preset level or fades lights to off.

        - Switch double tap raises light to full on level.

      - Switch Control: Switch single tap turns lights on/off.

The following products are based on Lutron Maestro Wireless 0-10 V Dimmer Sensor/Maestro Wireless Sensor Switch Series.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here. Visit www.lutron.com for data sheets and other information.

      - Product(s):

        - Passive Infrared 0-10 V Wall Dimmer Occupancy/Vacancy Sensor: 0-10 V control for 0-10 V fluorescent ballasts/LED drivers (8 A load at 120-277 V, 50 mA max control current); coverage of 900 square feet (81 sq m) with mounting height of 4 feet (1.2 m); 180 degree field of view; multi-location capability using wireless control stations with wallbox mounting adapter.

          - <<Type _____ - >>Sensor dimmer; occupancy/vacancy.

          - <<Type _____ - >>Sensor dimmer; vacancy-only.

          - <<Type _____ - >>Sensor switch; occupancy/vacancy.

          - <<Type _____ - >>Sensor switch; vacancy-only.

  - WIRELESS CONTROL STATIONS

    - General Requirements:

      - Communicates directly to compatible RF receiving devices through use of a radio frequency communications link.

Controls can be programmed with different functionality through system software without any hardware changes.

      - Allows for easy reprogramming without replacing unit.

      - Button Programming:

        - Single action.

        - Toggle action.

      - Includes LED to indicate button press or programming mode status.

      - Faceplates: Provide concealed mounting hardware.

      - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROLS - GENERAL REQUIREMENTS article above; White; Black; Ivory; Light Almond; White/Grey; As indicated on drawings; To be selected by Architect; or __________>>.

The Pico Wireless Control is a flexible and easy to use device that allows the user to control dimmers and switches. The Pico wireless control can function as a tabletop control on a pedestal, a lightweight handheld remote, or it can be wall-mounted with or without a Lutron Claro faceplate, to mimic a traditional keypad. The battery-operated control requires no external power or communication wiring. Models are available with integral night light. Visit www.lutron.com for data sheets and other information.

    - Battery Powered Wiredless Control Stations:

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Does not require external power packs, power or communication wiring.

      - Power: Battery-operated with minimum ten-year battery life (3-year battery life for night light models).

      - Mounting:

        - Capable of being mounted with a table stand or directly to a wall under a faceplate.

      - Product(s):

        - <<Type _____ - >>2-Button Control.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>2-Button Control with Night Light.

        - <<Type _____ - >>2-Button with Raise/Lower Control.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button Control.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control and Night Light.

        - <<Type _____ - >>4-Button.

          - Button Marking:  <<Zone controls (light); Scene keypads (light); 2-group controllers (lights); 4-group toggle; As indicated on drawings; or __________>>.

        - Single Pedestal.

        - Double Pedestal.

        - Triple Pedestal.

        - Quadruple Pedestal.

        - Screw Mounting Kit.

        - Wallbox Adapter.

    - Line-Powered Wireless Control Stations:

      - Power: 120-277 V.

      - Product(s):

        - <<Type _____ - >>2-Button Control.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>2-Button with Raise/Lower Control.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

  - LED DRIVERS

    - General Requirements:

Include the following paragraph to ensure that the driver is designed to operate at worst case environmental conditions without affecting product life.

      - Operate for at least 50,000 hours at maximum case temperature and 90 percent non-condensing relative humidity.

      - Provide thermal fold-back protection by automatically reducing power output (dimming) to protect LED driver and LED light engine/fixture from damage due to over-temperature conditions that approach or exceed the LED driver's maximum operating temperature at calibration point.

      - Provide integral recording of operating hours and maximum operating temperature to aid in troubleshooting and warranty claims.

Electrostatic charge builds up on people as a result of friction (walking across a carpet). When a person touches an electronic device, a discharge can occur and cause damage. Electrostatic discharge (ESD) testing is done according to the IEC 61000-4-2 standard (human body model). Testing should be completed on all user accessible points such as terminal blocks, buttons, and control inputs. The standard only describes how to conduct the test, which is why it is important to specify "without impairment of performance" as the pass/fail criteria.

      - Designed and tested to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

During manufacturing, ballasts are more susceptible to damage by electrostatic discharge (ESD). A facility that does not meet this requirement could have excessive defective units delivered to a job site.

      - Manufactured in a facility that employs ESD reduction practices in compliance with ANSI/ESD S20.20.

UL 8750 is a UL safety standard that covers LED drivers.

      - UL 8750 recognized or listed as applicable.

UL Type TL and UL Class P are UL ratings for an LED driver. LED drivers that are Type TL rated can be easily swapped in a fixture by the fixture manufacturer with lower re-testing time and certification cost. LED drivers that are Class P listed can be swapped without any re-testing time or certification cost.

      - UL Type TL rated or UL Class P listed where possible to allow for easier fixture evaluation and listing of different driver series.

If a driver needs to be replaced in the field, a UL recognized driver listed for field replacement under UL 1598C can be replaced with a like driver. Without a UL 1598C rating, you will either have to send the fixture back to the manufacturer or have UL re-inspect the fixture in the field. UL listed Class P drivers are also suitable for field replacement.

      - Suitable for field replacement as applicable; listed in accordance with UL 1598C or UL 8750, Class P as indicated.

A surge protector is sold as an accessory to a computer purchase to protect it from lightning strikes or other voltage surges. Likewise, dimmer circuit require surge protection. Surge protection can be built into a driver or it can be purchased separately as an external accessory. Include the following paragraph to ensure that the surge protection is built into the drivers.

      - Designed and tested to withstand Category A surges of 4,000 V according to IEEE C62.41.2 without impairment of performance.

The following means that the driver will be inaudible in a general office space (30dBA is a quiet whisper at 5 feet).

      - Class A sound rating; Inaudible in a 27 dBA ambient.

Line voltage fluctuates throughout the day as equipment (i.e. equipment or other buildings in the vicinity) come on line. Line voltage fluctuations will cause noticeable changes in light output. The driver automatically compensates for variations in voltage to provide constant light output.

      - Demonstrate no visible change in light output with a variation of plus or minus 10 percent change in line-voltage input.

      - LED drivers of the same family/series to track evenly across multiple fixtures at all light levels.

To meet the lighting density requirements of a job, the fixture OEM needs to deliver fixtures with custom lumen output levels. Programmable LED drivers allow the OEM to easily customize their fixtures. Full dimming range 100%-5% or 100%-1% must be achieved at any programmed level.

      - Offer programmable output currents in 10 mA increments within designed driver operating ranges for custom fixture length and lumen output configurations, while meeting a low-end dimming range of 100 to 0.1 percent, 100 to 1 percent or 100 to 5 percent as applicable.

The following paragraph ensures that electronic dimming drivers will meet NEMA inrush recommendations, reducing false circuit breaker tripping due to turn on inrush. NEMA 410 defines the worst case inrush current expected to be encountered in field installations, and establishes uniform testing criteria for compatibility between controls, ballasts, drivers, etc.

      - Meet NEMA 410 inrush requirements for mitigating inrush currents with solid state lighting sources.

LED drivers with fault protection ensure that a wiring mistake that results in up to 277 V being applied to the communication links on the driver will not damage the driver and require the fixture to be replaced at significant cost.

      - Employ integral fault protection up to 277 V to prevent LED driver damage or failure in the event of incorrect application of line-voltage to communication link inputs.

Sometimes, the driver cannot be installed within the fixture, e.g. a chandelier. A driver that is remote mountable allows you to place the driver in a convenient location, without affecting the dimming performance of the driver.

      - LED driver may be remote located up to 100 feet (30 m) from LED light engine depending on power outputs required and wire gauge utilized by installer.

    - 3-Wire Control:

Mis-wiring control wires and/or lamp wires can cause a driver to fail. Lutron includes fault protection circuitry in its drivers to survive common mis-wires.

      - Provide integral fault protection to prevent driver failure in the event of a mis-wire.

      - Operate from input voltage of 120 V through 277 V at 50/60 Hz.

Lutron's EcoSystem® is a commercial lighting control system that is comprised of digitally addressable dimming ballasts, controls, and environmental sensors. These components provide businesses with energy savings from 40 to 70%, while increasing space flexibility, improving occupant comfort and productivity, and reducing maintenance costs.

    - Digital Control (when used with compatible lighting control systems):

After a power interruption, the lights in the space should go back to where they were prior to the interruption without flashing to full, or requiring a manual intervention. Power failure memory prevents annoying interruption to work after a power interruption.

      - Employ power failure memory; LED driver to automatically return to the previous state/light level upon restoration of utility power.

      - Operate from input voltage of 120 V through 277 V at 50/60 Hz.

For emergency lighting applications with an ATS, the control system must turn on automatically and should not be overridden except by authorized persons.

      - Automatically go to 100 percent light output upon loss of control link voltage and lock out system commands until digital control link voltage is restored. Manufacturer to offer UL 924 compliance achievable through use of external interface upon request.

      - When normal power is lost, drivers fed with emergency power go to emergency mode.

      - Replacement of single driver during maintenance does not require reprogramming.

To simplify wiring, EcoSystem digital low voltage control wiring is able to be wired as either class 1 or class 2. Class 1 wiring allows the wiring to share a conduit with power wiring (where allowed by local codes) and reduce the cost of pulling control wiring in the ceiling.

      - Digital low-voltage control wiring capable of being wired as either Class 1 or Class 2.

    - Product(s):

Hi-lume® Premiere 0.1% Constant Voltage L3D0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - Digital Control, 0.1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance:

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates 0.25 W standby power at 120 V and 0.40 W standby power at 277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at maximum power; complies with ANSI C82.11.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected, open circuit protected, and overload protected.

        - Constant Voltage Drivers:

          - Support for cove and under-cabinet fixtures at 24 V.

            - Support LED arrays from 2 W to 96 W.

IEEE 1789 sets the minimum frequency for PWM dimming above 1250 Hz to reduce chances for any disturbance in video recording.

            - Pulse Width Modulation (PWM) dimming frequency meets IEEE 1789.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

Hi-lume® Premiere 0.1% Constant Voltage L3D0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - 3-Wire Control, 0.1 Percent Dimming:

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at maximum power; complies with ANSI C82.11.

A Class 2 output makes it easier and cheaper to design a fixture. It also allows simpler wiring for remote mounted LED drivers.

        - UL Class 2 output designed to withstand hot swap of LED loads.

        - Driver outputs to be short circuit protected, open circuit protected, and overload protected.

        - Constant Voltage Drivers:

          - Support for cove and under-cabinet fixtures at 24 V.

            - Support LED arrays from 2 W to 96 W.

IEEE 1789 sets the minimum frequency for PWM dimming above 1250 Hz to reduce chances for any disturbance in video recording.

            - Pulse Width Modulation (PWM) dimming frequency meets IEEE 1789.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

Hi-lume® Premier 0.1% Constant Current PEQ0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - Digital Control, 0.1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance:

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates less than 0.5 W standby power at 120/277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120/277 V.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected and open circuit protected.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

Hi-lume® 1% (PEQ1 Series) LED Drivers provide a high-performance solution for any space, in any application, while providing smooth, continuous dimming down to 1 percent of output current.

      - Digital Control, 1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance:

        - Dimming Range:  100 to 1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates less than 0.5 W standby power at 120/277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120/277 V.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected and open circuit protected.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

Hi-lume® 1% (LTE-Series) Driver is a high-performance LED driver that provides smooth, continuous 1% dimming for virtually any LED fixture, whether it requires constant current or constant voltage. It is the most versatile LED driver offered today due to its compatibility with a wide variety of LED arrays, multiple form factors, and numerous control options.

      - Forward Phase (Neutral Wire Required), One Percent Dimming:

        - Dimming Range:  100 to one percent relative light output.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at full output for 40 W loads; complies with ANSI C82.11.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 53 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for cove and under-cabinet fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

        - Constant Voltage Drivers:

          - Support for downlights and pendant fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for cove and under-cabinet fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

Hi-lume® 1% (L3D-Series) Driver is a high-performance LED driver that provides smooth, continuous 1% dimming for virtually any LED fixture, whether it requires constant current or constant voltage. It is the most versatile LED driver offered today due to its compatibility with a wide variety of LED arrays, multiple form factors, and numerous control options.

      - 3-Wire and Digital Control, One Percent Dimming:

        - Dimming Range:  100 to one percent relative light output.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120 V or 277 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at full output for loads greater than 25 W typical (higher for select models); complies with ANSI C82.11.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 53 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

          - Support for troffers, linear pendants, and linear recessed fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

          - Support for cove and under-cabinet fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

        - Constant Voltage Drivers:

          - Support for downlights and pendant fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

          - Support for troffers, linear pendants, and linear recessed fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

          - Support for cove and under-cabinet fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

5-Series (LDE5-Series) LED Drivers provide a high-performance solution for any space, in any application, while providing smooth, continuous dimming down to 5 percent of output current.

      - Digital Control, Five Percent Dimming:

        - Dimming Range:  100 to five percent measured output current.

        - Typically dissipates 0.2 W standby power at 120 V and 0.3 W standby power at 277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V.

        - Constant Current Reduction (CCR) dimming method.

        - Total Harmonic Distortion (THD):  Less than 21 percent at full load; complies with ANSI C82.11.

        - Constant Current Drivers:

The following is based on Lutron K-Case Form Factor drivers.

          - Support for downlights and pendant fixtures in currents from 220 mA to 1.4 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - UL listed Class P.

The following is based on Lutron M-Case Form Factor drivers.

          - Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 75 W.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in ENERGY STAR for Luminaires Version 2.0.

            - Models available to meet the DesignLights Consortium (DLC) power line quality requirements.

            - UL listed Class P.

Hi-lume® 1% Soft-on Fade-to-Black (LDE1-Series) LED Drivers provide a high-performance solution for any space, in any application, while providing smooth, continuous dimming down to 1 percent of output current.

      - Digital Control, One Percent Dimming with Soft-On and Fade-to-Black Low End Performance:

        - Dimming Range:  100 to one percent measured output current.

        - Features smooth fade-to-on and fade-to-black low end dimming performance for an incandescent-like dimming experience.

The following paragraph ensures that the LED drivers exceed Energy Star standards for standby power.

        - Typically dissipates 0.2 W standby power at 120 V and 0.3 W standby power at 277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V.

Constant current dimming eliminates the chance for any disturbance in video recording.

        - Employs true Constant Current Reduction (CCR) dimming method from 100 to five percent light level and Pulse Width Modulation (PWM) dimming method from five percent to off.

        - Pulse Width Modulation (PWM) frequency of 240 Hz.

        - Total Harmonic Distortion (THD):  Less than 20 percent at full output for drivers greater than 25 W; complies with ANSI C82.11.

A Class 2 output makes it easier and cheaper to design a fixture. It also allows simpler wiring for remote mounted LED drivers.

        - UL Class 2 output.

        - Driver outputs to be short circuit protected, open circuit protected, and overload protected.

        - Constant Current Drivers:

The following is based on Lutron K-Case Form Factor drivers.

          - Support for fixtures from 220 mA to 1.4 A over multiple operating ranges.

            - Support LED arrays up to 40 W.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in ENERGY STAR for Luminaires Version 2.0.

            - UL listed Class P.

The following is based on Lutron M-Case Form Factor drivers.

          - Support for fixtures from 150 mA to 2.1 A over multiple operating ranges.

            - Support LED arrays up to 75 W.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in ENERGY STAR for Luminaires Version 2.0.

            - Models available to meet the DesignLights Consortium (DLC) power line quality requirements.

            - UL listed Class P.

Do not include power interfaces if wired wall dimmers and switches are not included.

  - POWER INTERFACES

    - Provide power interfaces as indicated or as required to control the loads as indicated.

    - General Requirements:

Include the following paragraph to simplify field wiring for the installation contractor and prevent the failure of the interface due to phase to phase overvoltage.

      - Phase independent of control input.

      - Dimmer to meet limited short circuit test as defined in UL 508.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock. It is common for this leakage current to exceed 5 milliamps (the UL limit for GFCI outlets). Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

      - Utilize air gap off to disconnect the load from line supply.

      - Diagnostics and Service: Replacing power interface does not require re-programming of system or processor.

    - Product(s):

The following modules take phase control input and provide full circuit of forward/reverse phase control (16 amps) output. The output can be 120V or 277V. This is used for incandescent, magnetic low voltage (MLV), electronic low voltage (ELV), and neon/cold cathode.

      - Phase-Adaptive Power Module:  Provides interface for phase control input to provide full 16 A circuit output of forward/reverse phase control for compatible loads.

The following modules take phase control input and provide full circuit of control (16 amps) output to Lutron Hi-lume dimming ballasts. The output can be 120V or 277V.

      - 3-Wire Fluorescent Power Module:  Provides interface for phase control input to provide full 16 A circuit output for compatible line-voltage control fluorescent electronic dimming ballasts or LED drivers.

The following modules take phase control input and provide full circuit switching (16 amps) output. The output can be 120V or 277V. This is used for non-dim loads.

      - Switching Power Module: Provides interface for phase control or switched input to provide full 16 A circuit output of switching for compatible non-dim loads.

The following interfaces take phase control input and provide full circuit of switching and 0-10V low voltage output (16 amps) for electronic fluorescent ballasts.

      - Ten Volt Interface: Provides interface for phase control input to provide full 16 A circuit output of switching and 0-10 V low voltage control for compatible fluorescent electronic dimming ballasts or LED drivers.

  - DIGITAL DIMMING BALLAST MODULES

    - Provide digital dimming ballast modules as indicated or as required to control the loads as indicated.

    - General Requirements:

      - Provide continuous 3-wire signal dimming to compatible 3-wire electronic dimming ballasts.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock. It is common for this leakage current to exceed 5 milliamps (the UL limit for GFCI outlets). Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

      - Utilize air gap off to disconnect the load from line supply.

      - If power is interrupted and subsequently restored, lights automatically return to the setting prior to power interruption.

Digital addressable systems require reprogramming when ballasts and ballast modules fail. Without a visible unique serial ID, extensive documentation and additional support is required to replace multiple ballasts or modules.

      - Unique internal reference number visible displayed on module cover.

      - Dimmer to meet limited short circuit test as defined in UL 20.

Mis-wiring control wires and/or lamp wires can cause modules to fail. Lutron includes fault protection circuitry in its modules to survive common mis-wires.

      - Provide integral fault protection to prevent ballast module failure in the event of a mis-wire.

    - Product(s):

The following module is designed for installation to a 4 inch by 4 inch junction box.

      - 3-Wire Ballast Module, 16 Amp:

        - Integrates up to 16 amps of 3-wire electronic dimming ballasts into digital control system as a single zone.

        - Integrates up to 16 amps of switched high intensity discharge (HID) lighting load into digital control system as a single zone.

  - WIRELESS HUBS

    - Product(s):

--CHOOSE ONE OF THE TWO HUB TYPES BELOW--

      - Wireless hub without BACnet.

The following is based on Model HJS-0-FM.

        - Flush-mount wireless hub; supports up to 70 total paired devices.

The following is based on Model HJS-1-FM.

        - Flush-mount wireless hub; supports up to 700 total paired devices.

The following is based on Model HJS-1-SM.

        - Surface-mount wireless hub; supports up to 700 total paired devices.

      - Wireless hub with BACnet.

The following is based on Model HJS-2-FM.

        - Flush-mount wireless hub; supports up to 700 total paired devices.

The following is based on Model HJS-2-SM.

        - Surface-mount wireless hub; supports up to 700 total paired devices.

    - Integrated multicolor LED provides feedback on what mode the hub is in for simple identification and diagnosis.

    - Integrated processor and web server allows hub to set up and operate the system without any external connections to outside processors, servers, or the internet.

    - Utilizes Ethernet connection for:

      - Networking up to 64 hubs together to create a larger system.

      - Integration with Building Management System (BMS) via native BACnet; does not require interface (wireless hub with BACnet only).

      - Remote connectivity capabilities, including maintaining system date/time and receiving periodic firmware updates (requires internet connection).

    - A single hub or network of hubs can operate on either a dedicated lighting control only network or can be integrated with an existing building network as a VLAN.

    - Communicates directly to compatible RF devices through use radio frequency communications link; does not require communication wiring; RF range of 71 feet (23 m) through walls to cover an area of 15836 square feet (1471 sq m) (device and hub must be on the same floor).

    - Communicates directly to mobile device (smartphone or tablet) or computer using built-in Wi-Fi, 2.4 GHz 802.11b/g; wireless range of 71 feet (23 m) through walls (device and hub must be on the same floor).

      - Does not require external Wi-Fi router for connecting to the hub.

    - Allows for system setup, control, and monitoring from mobile device or computer using web-based software:

Any given load device can be controlled by 10 occupancy sensors, 10 Pico remote controls or 1 daylight sensor (Pico remote controls and sensors must be located within 30 ft (9 m) of the load device they are controlling.

      - Supports paired devices up to maximum number indicated including compatible wireless sensors, wireless control stations, and wireless load devices.

      - Allows for timeclock scheduling of events, both time of day and astronomic (sunrise and sunset).

        - Timeclock is integrated into the unit and does not require a constant internet connection.

        - Retains time and programming information after a power loss.

        - 365-day schedulable timeclock allows for:

          - Scheduling of events years in advance.

          - Setting of recurring events with exceptions on holidays.

        - Time clock events can be scheduled to:

          - Send lights to a desired level and select the fade rate desired to reach that level.

          - Adjust level lights go to when occupied.

          - Adjust level lights go to when unoccupied.

          - Enable/disable occupancy.

          - Adjust timeout of sensors (requires wired fixture sensor or wireless fixture control dongle with integral sensing capabilities).

          - Control individual devices, areas, or groups of areas. When connected to server, only areas or groups of areas can be controlled with timeclock events.

      - Daylighting:

        - Daylighting can be enabled/disabled. Can be used to override the control currently taking place in the space.

The following is particularly useful when new departments move into a space.

        - Daylight set point can be adjusted with the software to increase or decrease the electric light level in the room based on the same amount of natural light.

        - Reports measured energy for wireless fixture control dongle when paired with driver that supports measured power (measurement accuracy defined by driver specification) or reports calculated power if driver does not have measurement capabilities.

      - Allows for control, monitoring, and adjustment from anywhere in the world (wireless hub internet connection required).

      - Uses RF signal strength detection to find nearby devices for quick association and programming without having to climb ladders.

        - Association and setup does not require a factory technician to perform.

      - System using wireless hub(s) can operate with or without connection to the internet.

      - Supports energy reporting.

        - Reports measured energy data for fixture control modules at accuracy of plus/minus 2 percent or 0.5 W (whichever is higher).

        - Reports calculated energy data for junction box mounted modules at accuracy of 10 percent.

      - Supports automatic demand response for load shedding via:

        - Local contact closure without need for separate interface.

        - OpenADR® 2.0b compliant utility command.

        - BACnet (wireless hub with BACnet only).

      - Support automatic generation of alerts in web-based application for designated events/triggers, including:

        - Low-battery condition in battery-operated sensors and controls; alert cleared when battery is replaced.

        - Missing device (e.g., control or sensor); alert cleared when device is detected by system.

      - Wireless hub can be firmware upgraded to provide new software features and system updates.

        - Firmware update can be done either locally using a wired Ethernet connection or Wi-Fi connection, or remotely if the wireless hub is connected to the internet.

    - Web-Based Application:

      - Accessibility and Platform Support:

        - Web-based; runs on most HTML5 compatible browsers (including Safari and Chrome).

        - Supports multiple platforms and devices; runs from a tablet, desktop, laptop, or smartphone.

        - User interface supports multi-touch gestures such as pinch to zoom, drag to pan, etc.

        - Utilizes HTTPS (industry-standard certificate-based encryption and authentication for security).

        - Multi-level Password Protected Access:  Individual password protection on both the integrated Wi-Fi network and web-based software.

        - WPA2 security for Wi-Fi communication with wireless hub.

      - System Navigation and Status Reporting:

        - Area Tree View:  Easy navigation by area name to view status and make programing adjustments through the software.

        - Area and device names can be changed in real time.

      - Setup app available for iOS and Android that allows for:

        - Job registration to extend product warranty.

        - Management of setup for multiple projects in different locations.

        - Creation of handoff documents that are sent directly to a facility manager via email once setup is complete.

        - Backup of wireless hub database to cloud for hub replacement.

        - Access to native help and instructions to assist user with system setup.

    - BACnet Integration (wireless hub with BACnet only):

      - Provide ability to communicate by means of native BACnet IP communication (does not require interface) to lighting control system from a user-supplied 10BASE-T or 100BASE-T Ethernet network.

      - Requires only one network connection per hub.

      - BACnet Integrator Capabilities:

        - The BACnet integrator can command:

          - Area light output.

          - Area load shed level.

          - Area load shed enable/disable.

          - Enable/Disable:

            - Area occupancy sensors.

            - Area daylighting.

          - Daylighting level.

          - Area occupied and unoccupied level

          - Occupancy sensor timeouts (for fixture sensors).

        - The BACnet integrator can monitor:

          - Area on/off status.

          - Area occupancy status.

          - Area load shed status.

          - Area instantaneous energy usage and maximum potential power usage.

          - Enable/Disable:

            - Area occupancy sensors.

            - Daylighting.

            - Timeclocks.

          - Daylighting level.

          - Light levels from photo sensors.

          - Area occupied and unoccupied level.

          - Occupancy sensor timeouts.

    - API Integration:

      - Support communication, without requiring interface, between lighting control system and third-party systems via RESTful API.

      - Requires one network connection per wireless hub.

      - API Integration Capabilities:

        - Control all zones or subset of zones.

          - Set zones in designated area to specific level.

          - Raise/lower dimmable lights in designated area.

        - Control individual zones.

        - Subscribe to and Monitor:

          - Area status changes (e.g., occupancy, light level, and instantaneous power).

          - Individual zone changes in light level.

          - Alerts (e.g., missing device and low battery).

    - Scenes:

      - Support programmable scenes to control individual devices, areas, or groups of areas on demand.

      - Scenes may be activated via:

        - Contact closure input.

        - API integration.

        - Manual activation in app.

    - Emergency Mode:

        - Support emergency mode to, when triggered, send lights to defined levels and lock out controls for load control modules equipped with emergency mode.

      - Emergency mode may be activated via:

        - Contact closure input.

        - API integration.

        - Manual activation in app.

Contact closure inputs provide integration with devices by others including devices for Title 24 Automatic Demand Response

• Contact closure inputs on multiple hubs can be wired in parallel. DO NOT wire inputs in parallel with other equipment as it can cause the inputs on either of the devices to falsely trigger.

• To ensure proper operation of contact closure inputs, a PS-J-20W-UNV power supply may not be used to provide power to more than one hub.

    - Contact Closure Interface:  Provide two contact closure inputs; accepts both momentary and maintained contact closures that can be used for automatic demand response.

    - Rated for use in air-handling spaces as defined in UL 2043.

Visit www.lutron.com for more information on California Title 24 requirements.

    - Meets CAL TITLE 24 P6 requirements.

Wiring distance for any single inter-hub wiring link segment is 330 ft (100 m) max; use Lutron-provided Ethernet switches for longer distances

    - Provide Ethernet switch(es) as required for inter-hub network wiring per manufacturer’s instructions; do not exceed manufacturer’s required maximum wiring segment lengths.

      - Product(s):

        - 16 port.

        - 24 port.

        - 24 port, 1 multi-mode fiber.

        - 24 port, 2 multi-mode fiber.

        - 24 port, 1 single-mode fiber.

        - 24 port, 2 single-mode fiber.

  - SOFTWARE DATA AND ANALYTICS DASHBOARD

    - Control and Monitor Software:

      - General Requirements:

        - Web-based; runs on most HTML5 compatible browsers (including Internet Explorer, Chrome, and Safari).

        - Supports multiple platforms and devices; runs from a tablet, desktop, laptop, or smartphone; optimized for displays of 1024 by 768 pixels or higher.

        - User interface supports multi-touch gestures such as pinch to zoom, drag to pan, etc.

        - Utilizes HTTPS (industry-standard certificate-based encryption and authentication for security).

        - All functionality listed below must be available via a single application.

      - System Navigation and Status Reporting:

        - Performed using graphical floor plan view or a generic system layout.

        - Graphical Floor Plan View:  Utilizes customized CAD based drawing of the building. Pan and zoom feature allows for easy navigation; dynamically adjusts the details presented based on zoom level.

      - Control of Lights:

        - Control and monitor zone/area lights.

          - Area lights can be monitored for on/off status from a graphical floor plan or generic system layout.

          - All lights in an area can be turned on/off (dimmable lights can also be dimmed up/down from current level).

      - Occupancy:

        - Area occupancy can be monitored.

          - Can be monitored graphically if a graphical floor plan has been created.

          - Can be monitored historically in space utilization reports.

        - Scheduled events can be created to change occupancy parameters as described under “Scheduling” below.

      - Load Shedding: View current load shed status (active/inactive) for each wireless hub and enable/disable load shed for the entire building/system.

      - Scheduling: Schedule time of day and astronomic time clock events to automate functions.

        - Scheduled events can control the following:

          - Area light levels for all dimmable lights in an area.

          - On/off status of all switched lights and contact-closure outputs in an area.

          - On/off status of all switched receptacles in an area.

        - Scheduled events can be created to change the following occupancy parameters:

          - Enable/disable sensors.

          - Change occupancy mode (auto-on/auto-off versus manual-on/auto-off).

          - Adjust occupied and/or unoccupied level.

          - For compatible individual fixture sensors, sensor timeout can be adjusted.

        - Easily monitor and adjust scheduled events using a weekly calendar view.

      - Reporting: Provide reporting capability that allows the building manager to gather real-time and historical information about the system as follows:

        - Energy Reports: Show a comparison of cumulative energy used over a period of time for one or more areas.

        - Power Reports: Show power usage trend over a period of time for one or more areas.

        - Space Utilization/Occupancy Reports:  Show historical occupancy over a period of time for one or more areas using a graphical floor plan, generic system layout, and graphs and charts.

      - Administration:

        - Users: Allows new user accounts to be created and existing user accounts to be edited.

          - Supports Active Directory (LDAP) tying user accounts to network accounts.

        - Area and feature access can be restricted based on login credentials.

        - Supports up to 20 concurrent users and 10,000 user accounts.

      - Devices/Settings Adjustment:

        - Users with appropriate permissions can navigate to the wireless hub setup screens in order to view and/or adjust specific settings for areas or devices (including load shed settings, daylighting settings, device associations and programming, occupancy settings, high-end/low-end trim settings, etc).

      - Control and Monitor for Multiple Systems:

        - Allows user to view aggregate data from multiple connected systems spanning multiple buildings through a single user account:

          - Space utilization/occupancy.

          - Energy usage/savings.

        - Allows user to view details and adjust settings for any connected system; supports system navigation through campuses and buildings using graphical floor plans.

    - Computers:

      - Server:

        - Suitable for 24 hour per day, 7 day per week programming, monitoring, control, and data logging of digital-network lighting controls.

        - Suitable to handle client machine request in multi-computer systems.

        - Unless otherwise indicated, computer to be provided <<by lighting control system manufacturer; by others, meeting lighting control system manufacturer's minimum requirements; or __________>>.

        - Minimum Hardware Requirements:

          - Processor: Quad Core Intel® Xeon®.

          - 8 GB Ram.

          - 250 GB hard drive (40 GB for application and database).

          - Two 10/100/1000 Ethernet network interfaces - one for communication with lighting management hubs and one for communication with corporate intranet to allow access from system PCs and/or energy saving display terminals. Only one Ethernet network interface is required if all lighting management hubs and client PCs are on the same network.

          - Monitor with 1280 x 1024 resolution.

          - 4 USB 2.0 ports.

          - Dedicated Graphics Card with 256 MB of memory (only required if running client software from the server).

        - Minimum Software Requirements:

          - Licensed installation of US English 64-bit Microsoft® Windows® Server 2008 R2, Windows Server 2012 R1, or Windows Server 2012 R2.

          - Microsoft® Internet Information Services (IIS) 7 or later.

          - Microsoft® Internet Explorer 9 or later.

          - Microsoft® .NET Framework 3.5.

          - Microsoft® .NET Framework 4.5.

      - Computers Provided by Lighting Control System Manufacturer: Computer software to be preinstalled and tested prior to shipping.

  - ACCESSORIES

    - Emergency Lighting Interface:

Lutron's Application Note #106 contains more information on emergency lighting systems.

      - Provides total system listing to UL 924 when used with lighting control system.

      - Senses all three phases of building power.

      - If power on any phase fails provides output to send lights controlled to defined levels. Lights to return to their previous intensities when normal power is restored.

      - Accepts contact closure input from fire alarm control panel.

  - SOURCE QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - Factory Testing:

To ensure that 100 percent of the lighting control products work at installation, the manufacturer should test 100 percent of all assemblies at full rated load in the factory. This testing will assure that every product has been tested and guaranteed to work. Sampling would only prove that the samples work and should not be acceptable.

      - Perform full-function factory testing on all completed assemblies. Statistical sampling is not acceptable.

To ensure that 100 percent of the lighting control products work at installation, the manufacturer should test 100 percent of all ballasts at the factory.

      - Perform full-function factory testing on 100 percent of LED drivers.

- EXECUTION

  - EXAMINATION

    - Verify that field measurements are as shown on the drawings.

    - Verify that ratings and configurations of system components are consistent with the indicated requirements.

    - Verify that mounting surfaces are ready to receive system components.

    - Verify that conditions are satisfactory for installation prior to starting work.

  - PREPARATION

Use the following paragraph to specify an optional visit for system and network integration consultation. Edit the choice to have this additional value included as an alternate or as part of the base bid.

A System and Network Integration Consultation is required for a job that will integrate with a third party BMS system.

    - System and Network Integration Consultation: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to conduct meeting with facility representative and other related equipment manufacturers to discuss equipment and integration procedures.

      - Coordinate scheduling of visit with Lighting Control Manufacturer. Manufacturer recommends that this visit be scheduled early in construction phase, after system purchase but prior to system installation.

  - INSTALLATION

    - Perform work in a neat and workmanlike manner in accordance with NECA 1 and, where applicable, NECA 130<<, except for mounting heights specified in those standards;, including mounting heights specified in those standards unless otherwise indicated; or __________>>.

    - Install products in accordance with manufacturer's instructions.

    - Sensor Locations:

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS".

      - Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS", locate sensors in accordance with layout provided by Lighting Control Manufacturer. Lighting Control Manufacturer may direct Contractor regarding sensor relocation should conditions require a deviation from locations indicated. Where Lighting Control Manufacturer Sensor Layout and Tuning service is not specified, locate sensors in accordance with Drawings.

      - Sensor locations indicated are diagrammatic. Within the design intent, reasonably minor adjustments to locations may be made in order to optimize coverage and avoid conflicts or problems affecting coverage, in accordance with manufacturer's recommendations.

Interior sensors work mainly with diffused light, as such, they have a much higher lighting gain than exterior sensors. Electric light sources can affect these sensors unless the sensors are shielded from the light given off by electric light sources.

    - Ensure that daylight sensor placement minimizes sensor view of electric light sources. Locate ceiling-mounted and luminaire-mounted daylight sensors to avoid direct view of luminaires.

Many lamp manufacturers recommend seasoning fluorescent lamps prior to dimming in order to ensure full rated life.

    - Lamp Burn-In: Operate lamps at full output for prescribed period per manufacturer's recommendations prior to use with any dimming controls. Replace lamps that fail prematurely due to improper lamp burn-in.

If the lamp leads exceed the specification, trouble starting the lamps may result.

    - LED Light Engine/Array Lead Length: Do not exceed 100 feet (31 m).

    - Identify system components in accordance with Section 26 0553.

  - FIELD QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

Edit the choice in the following paragraph to indicate whether or not Lutron Full-Scope Start-Up Service will be required. Keep in mind however that without Lutron Start-Up Service, Standard Warranty coverage is significantly reduced. Coordinate with warranty requirements specified in Part 1 under "WARRANTY".

    - Manufacturer's Full-Scope Start-Up Service <<is not required; is required; or __________>>.

If Lutron Full-Scope Start-Up Service is not specified in the paragraph above, the following paragraph may be used to specify optional manufacturer programming services, available for purchase in blocks of time for either on-site or remote programming.

    - Manufacturer’s Programming Service:

      - Product(s):

        - On-site programming, 8-hour block.

        - On-site programming, 4-hour block.

        - Remote programming, 4-hour block.

      - Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer to perform <<on-site; remote; or __________>> programming tasks for <<8 hours; or __________>>.

      - Furnish unit prices for each available programming time interval.

Use the following paragraph only if Lutron Full-Scope Start-Up Service is specified in the paragraph above. Edit the choice to indicate if On-Site Start-Up Service is required or if Remote Start-Up is preferred where possible (Lutron will quote On-Site Start-Up Service if required due to system size and other system characteristics). Either Full-Scope On-Site Start-Up or a Warranty Audit Visit is required if Lutron Silver, Gold, or Platinum Enhanced Warranties are specified in Part 1 under "WARRANTY".

    - Manufacturer's Full-Scope Start-Up Service: <<Utilize manufacturer's Remote Full-Scope Start-Up Service where possible. Provide On-Site Full-Scope Start-Up Service where required by manufacturer; Provide manufacturer's On-Site Full-Scope Start-Up Service; or __________>>.

      - Remote Full-Scope Start-Up Service: When available in accordance with manufacturer's guidelines, provide access to manufacturer's certified remote startup technician to provide instruction and guidance for complete system functional test.

      - On-Site Full-Scope Start-Up Service: Manufacturer's authorized Service Representative to conduct site visit upon completion of lighting control system installation to perform system startup and verify proper operation:

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS".

        - Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS", authorized Service Representative to verify sensor locations, in accordance with layout provided by Lighting Control Manufacturer; Lighting Control Manufacturer may direct Contractor regarding sensor relocation should conditions require a deviation from locations indicated.

        - Verify connection of power wiring and load circuits.

        - Verify connection and location of controls.

        - Energize wireless hubs.

        - Associate occupancy/vacancy sensors, daylight sensors, wireless remotes, and wall stations to load control devices.

        - Provide initial rough calibration of sensors; fine-tuning of sensors is responsibility of Contractor unless provided by Lighting Control Manufacturer as part of Sensor Layout and Tuning service where specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS".

        - Program timeclock schedules per approved sequence of operations.

        - Configure load shed parameters per approved sequence of operations.

        - Verify system operation control by control.

        - Obtain sign-off on system functions.

        - Train Owner's representative on system capabilities, operation, and maintenance, as specified in Part 3 under "Closeout Activities".

Use the following paragraph to specify startup of lighting control system outside normal business hours (at an additional cost). Edit the choice to have this additional cost included as an alternate or as part of the base bid.

      - After Hours Startup: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs to perform manufacturer's start-up procedures outside normal working hours (Monday through Friday, 7am to 5pm).

    - Correct defective work, adjust for proper operation, and retest until entire system complies with contract documents.

  - ADJUSTING

Use the following paragraph to specify an optional on-site meeting with the Lighting Control Manufacturer to make adjustments to the lighting control system, after all equipment and room furnishings have been installed (at an additional cost). Edit the first choice to have this additional cost included as an alternate or as part of the base bid.

This meeting may be desired in order to meet the lighting designer's original design intent. These adjustments may include light level, fade time and delay in lighting scenes.

    - On-Site Scene and Level Tuning: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to visit site to conduct meeting with <<Engineer; Owner's representative; Lighting Designer; or __________>> to make required lighting adjustments to the system for conformance with original design intent.

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS".

    - Sensor Fine-Tuning: Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "LIGHTING CONTROLS - GENERAL REQUIREMENTS", Lighting Control Manufacturer to provide up to two additional post-startup on-site service visits for fine-tuning of sensor calibration. Where Lighting Control Manufacturer Sensor Layout and Tuning service is not specified, Contractor to provide fine-tuning of sensor calibration.

  - CLEANING

    - Clean exposed surfaces to remove dirt, paint, or other foreign material and restore to match original factory finish.

  - COMMISSIONING

    - See Section 01 9113 for commissioning requirements.

Use the following paragraph to specify that lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) be performed by Lighting Control Manufacturer. Edit the second choice to have this additional cost included as an alternate or as part of the base bid.

Required documentation associated with this service is also specified in Part 1 under “SUBMITTALS”.

    - Title 24 Acceptance Testing Service: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to perform lighting control acceptance testing in accordance with CAL TITLE 24 P6. Submit required documentation.

  - CLOSEOUT ACTIVITIES

    - See Section 01 7800 - Closeout Submittals, for closeout submittals.

    - See Section 01 7900 - Demonstration and Training, for additional requirements.

    - Demonstration:

      - Demonstrate proper operation of lighting control devices to <<Engineer; or __________>>, and correct deficiencies or make adjustments as directed.

Use the following paragraph to specify an optional on-site walkthrough to demonstrate system functionality (at an additional cost). Edit the first choice to have this additional cost included as an alternate or as part of the base bid.

An on-site walkthrough to demonstrate system functionality to a commissioning agent is often required for LEED projects, other projects which involve a commissioning agent, or Title 24 (California) projects. During this visit, the manufacturer's authorized Service Representative will perform tasks, at the request of the facility representative or commissioning agent, such as to demonstrate wall control functions, explain timeclock schedules or describe occupancy or daylight sensor functionality.

      - On-Site Performance-Verification Walkthrough: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for lighting control manufacturer to provide on-site demonstration of system functionality to <<commissioning agent; facility representative; or __________>>.

    - Training:

Lutron's standard on-site full-scope start-up procedure for Vive system includes training of customer representatives. Include the paragraph below to specify additional training visits.

      - Include services of manufacturer's certified service representative to perform on-site training of Owner's personnel on operation, adjustment, and maintenance of lighting control system as part of on-site system start-up services.

Lutron's standard on-site full-scope start-up procedure for Vive system includes training of customer representatives. Use this paragraph to specify additional training visits (at an additional cost). Edit the first choice to have this additional cost included as an alternate or as part of the base bid. Edit the number of training days required according to project requirements.

      - Customer-Site Solution Training Visit: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to provide <<one; or _____>> day(s) of additional on-site system training.

Use the following paragraph to specify an on-site warranty audit visit, which is required for validation of Lutron Silver, Gold, or Platinum Enhanced Warranties unless On-Site Start-Up Service is specified.

    - On-Site Warranty Audit Visit:  Where Manufacturer On-Site Full-Scope Start-Up Service is not provided, include services of manufacturer to perform on-site verification that system meets manufacturer’s requirements as necessary for validation of specified enhanced warranty.

  - MAINTENANCE

    - See Section 01 7000 – Execution and Closeout Requirements, for additional requirements relating to maintenance service.

Use the following paragraph to specify an on-site meeting between the Lighting Control System Manufacturer and a facility representative to evaluate the system usage after the building has been in operation for a predetermined period of time (at an additional cost). Edit the first choice to have this additional cost included as an alternate or as part of the base bid.

This evaluation can include sensor calibration, timeclock programming, light level analysis, sensor layout support, and training. Edit the time period according to project requirements.

    - System Optimization Visit: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control System Manufacturer to visit site <<six months; or __________>> after system start-up to evaluate system usage and discuss opportunities to make efficiency improvements that will fit with the current use of the facility.

  - PROTECTION

    - Protect installed products from subsequent construction operations.

END OF SECTION