Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Lutron Electronics Co., Inc. ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Lutron Electronics Co., Inc., 7200 Suter Rd., Coopersburg, PA 18036; Phone: (610) 282-3800; Website: http://www.lutron.com/en-US/; Email: CustSvc@lutron.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 260943.23 - RELAY-BASED LIGHTING CONTROLS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED v4, LEED v4.1, IgCC, and Green Globes..

- GENERAL

      - SUMMARY

        - Section Includes:

          - Lighting control relay panels.

          - Networked lighting control panels.

          - Lighting control unit.

          - Manual switches and plates.

          - Field-mounted signal sources.

          - Conductors and cables.

        - Related Requirements:

Always retain two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - Monitoring: Acquisition, processing, communication, and display of equipment status data, metered electrical parameter values, power quality evaluation data, event and alarm signals, tabulated reports, and event logs.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for control modules, power distribution components, relays, manual switches and plates, and conductors and cables.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

          - Sound data including results of operational tests of central dimming controls.

          - Operational documentation for software and firmware.

        - Shop Drawings: For each relay panel and related equipment.

          - Include dimensioned plans, elevations, sections, and details. Include tabulations of installed devices, equipment features, and ratings.

          - Detail enclosure types and details for types other than Type 1.

          - Detail wiring partition configuration, current, and voltage ratings.

          - Short-circuit current rating of relays.

          - Address Drawing: Reflected ceiling plan and floor plans, indicating connected luminaires, address for each luminaire, and luminaire groups. Base plans on construction plans, using the same legend, symbols, and schedules.

          - Point List and Data Bus Load: Summary list of all control devices, sensors, ballasts, and other loads. Include percentage of rated connected load and device addresses.

          - Wire Termination Diagrams and Schedules: Coordinate nomenclature and presentation with Drawings and block diagram. Differentiate between manufacturer-installed and field-installed wiring.

Retain "Block Diagram" Subparagraph below when control is digital, PC or IP based.

          - Block Diagram: Indicate interconnections between components specified in this Section and devices furnished with power distribution system components. Indicate data communication paths and identify networks, data buses, data gateways, concentrators, and other devices to be used. Describe characteristics of network and other data communication lines.

Retain subparagraph below to require lighting controls to be connected to Section 230923 "Direct Digital Control (DDC) System for HVAC" or other integrated control system.

          - Submit evidence that lighting controls are compatible with connected monitoring and control devices and systems specified in [Section 230923 "Direct Digital Control (DDC) System for HVAC."] <Insert Section number and title.>

            - Show interconnecting signal and control wiring, and interface devices that show compatibility of inputs and outputs.

            - For control interfaces and adapters, list network protocols and provide statements from manufacturers that input and output devices comply with interoperability requirements of the protocol.

Retain "Field Quality-Control Submittals" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

        - Sample warranties.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

        - Extra Stock Material: Furnish extra materials to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Lighting Control Relays: Equal to <Insert number> percent of amount installed[ for each size indicated], but no fewer than <Insert number>.

      - DELIVERY, STORAGE, AND HANDLING

        - Handle and prepare panels for installation in accordance with NECA 407.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under the Contractor's general warranty and prevailing local laws.

Verify duration of extended warranty periods needed.

        - Special Manufacturer Extended Warranty: Manufacturer warrants that components of standalone multipreset modular dimming controls perform in accordance with specified requirements and agrees to provide repair or replacement of components that fail to perform as specified within extended warranty period.

          - Initial Extended Warranty Period: [Two] [Three] [Four] <Insert number> year(s) from date of Substantial Completion, for labor, materials, and equipment.

          - Follow-on Extended Warranty Period: [Eight] <Insert number> year(s) from date of Substantial Completion, for materials that failed because of transient voltage surges only, f.o.b. the nearest shipping point to Project site.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SYSTEM DESCRIPTION

        - Sequence of Operations: Input signal from field-mounted manual switches, or digital signal sources, must open or close one or more lighting control relays in the lighting control panels. Any combination of inputs must be programmable to any number of control relays.

Retain "Interface with HVAC DDC System" Paragraph below for interface with the HVAC DDC system. Coordinate with Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Interface with HVAC DDC System: Hardware and software must interface with HVAC DDC system to monitor, control, display, and record data for use in processing reports. Comply with requirements in Section 230923 "Direct Digital Control (DDC) System for HVAC."

Retain "Hardwired Points" or "Communication Interface" Subparagraph below. Retain first subparagraph if interface with the HVAC DDC system is through hardwired points and minimal interface is required. Retain second if extensive interface with the HVAC DDC system is required and is beyond what hardwired points can provide. Requirement may exclude some manufacturers. Coordinate with Section 230923 "Direct Digital Control (DDC) System for HVAC" or other integrated control system.

          - Hardwired Points:

            - Monitoring: On-off status, <Insert monitoring point>.

            - Control: On-off operation, <Insert control point>.

          - Communication Interface: Comply with [ASHRAE 135] [ISO/IEC 14908-1] ["MODBUS Application Protocol Specification"] <Insert type of interface>. The communication interface must enable the HVAC DDC system operator to remotely control and monitor lighting from a HVAC DDC system operator workstation. Control features and monitoring points displayed locally at lighting panel must be available through the HVAC DDC system. Comply with requirements in Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Surge Protective Device: Factory installed as an integral part of control components or field-mounted surge suppressors complying with UL 1449, SPD Type 2.

        - Electrical Components, Devices, and Accessories: Listed and labeled in accordance with NFPA 70 by qualified electrical testing laboratory recognized by authorities having jurisdiction and marked for intended location and application.

        - Comply with 47 CFR 15, Subparts A and B, for Class A digital devices.

        - Comply with UL 916.

Retain one of first two articles below. "Lighting Control Relay Panels" Article is for a single lighting control relay panel, typically not more than 42 relays. Retain "Networked Lighting Control Panels" Article for multiple panels networked under unified control and with an optional connection to the HVAC DDC system.

      - LIGHTING CONTROL RELAY PANELS

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; Energi Savr Node or comparable product by one of the following:

          - Cooper Industries, Inc.

          - Leviton Manufacturing Co., Inc.

          - <Insert manufacturer's name>.

        - Description: Standalone lighting control panel using mechanically latched relays to control lighting and appliances.

        - Lighting Control Panel:

          - A single enclosure with incoming lighting branch circuits, control circuits, switching relays, and on-board timing and control unit.

          - Minimum Number of Branch Circuits: Four.

          - A vertical barrier separating branch circuits from control wiring.

        - Relays:

          - Electrically operated, mechanically held single-pole switch, rated at 16 A at 277 V(ac), 0.5 hp at 120 V(ac) and 1.5 hp at 277 V(ac). Short-circuit current rating must be not less than 5 kA. Control must be three-wire, 24 V(ac).

        - Power Supply: NFPA 70, Class 2, sized for connected equipment, plus 20 percent spare capacity. Powered from a dedicated branch circuit of the panelboard that supplies power to the line side of the relays, sized to provide control power for the local panel-mounted relays, bus system, low-voltage inputs, field-installed occupancy sensors, and photo sensors.

Alternatives to "Operator Interface" Paragraph below are available from some manufacturers. Alternatives include handheld portable PCs, personal digital assistants, and mobile telephones.

        - Operator Interface:

          - Integral alphanumeric keypad and digital display, and intuitive drop-down menus to assist in programming.

          - Log and display relay on-time.

          - Connect relays to one or more time and sequencing schemes.

      - NETWORKED LIGHTING CONTROL PANELS

Revise this article for selected control protocol based on the need for flexibility, interoperability, and the most appropriate user interface.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; Energi Savr Node or comparable product by one of the following:

          - Cooper Industries, Inc..

          - Leviton Manufacturing Co., Inc.

          - <Insert manufacturer's name>.

        - Description: Lighting control panels using mechanically latched relays to control lighting and appliances. The panels must be capable of being interconnected with digital communications to appear to the operator as a single lighting control system.

        - Lighting Control Panels:

          - A single enclosure with incoming lighting branch circuits, control circuits, switching relays, and on-board timing and control unit.

          - Minimum Number of Branch Circuits: Four.

          - A vertical barrier separating branch circuits from control wiring.

        - Network Control Unit:

          - Ethernet Communications: Comply with [TCP/IP] <Insert network protocol> protocol. The main control unit shall provide for programming of all control functions of the main and all networked slave lighting control panels including timing, sequencing, and overriding.

Retain "Protocol" Subparagraph below for HVAC DDC system control network. Revise as required for other network protocols. See "Communication Networks for Lighting Controls" Article in the Evaluations for discussion of communication network options.

          - Protocol: Controllers must support serial MS/TP and Ethernet IP communications in accordance with [ASHRAE 135] [ISO/IEC 14908-1] ["MODBUS Application Protocol Specification"], and must be able to communicate directly via DDC system for HVAC TIA-485 serial networks and Ethernet 10Base-T networks as a native device.

        - Relays:

Retain one of two subparagraphs below. Not all listed manufacturers can comply with requirements when retaining second subparagraph. Two-pole relays are available from some manufacturers. See the Evaluations for discussion of additional relay features.

          - Electrically operated, mechanically held single-pole switch, rated at 16 A at 277 V(ac), 0.5 hp at 120 V(ac) and 1.5 hp at 277 V(ac). Short-circuit current rating must be not less than 5 kA. Control must be [three-wire, 24 V(ac)] [digital control network].

        - Power Supply: NFPA 70, Class 2, UL listed, sized for connected equipment, plus not less than 20 percent spare capacity. Powered from a dedicated branch circuit of the panelboard that supplies power to the line side of the relays, sized to provide control power for the local panel-mounted relays, bus system, low-voltage inputs, field-installed occupancy sensors, and low-voltage photo sensors.

        - Operator Interface: Interface for an Ethernet connection of Apple iPhone or iPod touch mobile device  for configuring all networked lighting control panels using mobile device application designed for the specified operating system. Include training of Owner's personnel.

        - Software:

          - Menu-driven data entry.

          - Online and offline programming and editing.

          - Provide for entry of the room or space designation for the load side of each relay.

          - Monitor and control all relays, indicating actual relay state and the name of the automatic actuating control, if any.

          - Size the software appropriate to the system.

      - LIGHTING CONTROL UNIT

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; [Grafik Eye QS] [QS Timeclock] or comparable product by one of the following:

          - Cooper Industries, Inc.

          - Leviton Manufacturing Co., Inc.

          - <Insert manufacturer's name>.

        - Features:

          - Timing Unit:

            - 365-day calendar, astronomical clock, and automatic adjustments for daylight savings and leap year.

            - Clock configurable for 12-hour (A.M./P.M.) or 24-hour format.

            - Schedule periods settable to the minute.

            - Day-of-week, day-of-month, day-of-year with one-time or repeating capability.

            - Special Date Periods: [10] <Insert number>.

          - Sequencing Control with Override:

            - Automatic sequenced on and off switching of selected relays at times set at the timing unit, allowing timed overrides from external switches.

            - Sequencing control must operate relays one at a time, completing the operation of all connected relays in not more than 10 seconds.

            - Override control allows any relay connected to be switched on or off by a field-deployed manual switch or by an automatic switch, such as an occupancy sensor.

            - Override control "blink warning" to warn occupants approximately [five minutes] <Insert time> before actuating an off sequence.

          - Contact Closure Input:

            - Voltage-free (dry) contact input, configurable for normally open (N.O.) or normally closed (N.C.) operation.

            - Configurable to activate scenes using momentary or maintained closure.

Retain "Shade Control" Subparagraph below if Project requires control of motorized shades.

          - Shade Control: Control switches, with LED indictors for motorized shades including open, one preset position, closed, raise and lower for [one] [two] [three] shade group(s).

          - Nonvolatile memory must retain all setup configurations. After a power failure, the controller must automatically reboot and return to normal system operation, including accurate time of day and date.

Retain one of two subparagraphs below, or both, if Project requires the extended functions of the Lutron's "Grafik Eye QS" lighting control unit.

          - Capable of manual control via wall station or IR receiver with compatible IR remote control.

          - Capable of automatic control based on input through a communication link with the following compatible devices:

            - Wireless Input Devices: Including daylight sensors, occupancy sensors, or control stations.

              - Minimum Wireless Range: 30 ft. (9 m).

              - Supports up to 30 wireless devices.

      - MANUAL SWITCHES AND PLATES

Coordinate use of manual switches in this article with required control and override functions, with occupancy sensor applications where used, and with switch and wall-plate finish specified in Section 262726 "Wiring Devices."

        - Push-Button Switches: Modular, momentary contact, three wire, for operating one or more relays and to override automatic controls.

          - Match color and style specified in Section 262726 "Wiring Devices."

Retain both subparagraphs below if required.

          - Integral green LED pilot light to indicate when circuit is on.

          - Internal white LED locator light to illuminate when circuit is off.

        - Cover Plates: Single and multigang plates as specified in Section 262726 "Wiring Devices."

        - Legend: Engraved or permanently silk-screened on cover plate where indicated. Use designations indicated on Drawings.

      - WIRED CONTROL STATIONS

        - General Requirements:

          - Power: Class 2 (low voltage).

          - UL listed.

          - Faceplates with concealed mounting hardware.

          - Borders, Logos, and Graduations: Scratch- and chemical-resistant, [laser-engraved] [silk-screened] graphics.

        - Multi-Scene, Wired, Keypad Control Stations:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; [Architrave] [seeTouch QS] [Signature Series] or comparable product by one of the following:

            - Cooper Industries, Inc.

            - Leviton Manufacturing Co., Inc.

            - <Insert manufacturer's name>.

          - Features:

            - Allows control of any device connected to control.

            - Replacement of unit does not require reprogramming.

            - Communications: RS 485.

            - Engraved keypads with button, zone, and scene descriptions.

            - Software Configuration:

              - Buttons programmable to perform a single defined action.

              - Buttons programmable to perform a defined action when depressed and defined action upon release.

              - Buttons programmable using conditional logic based on state variable such as time of day or partition status.

              - Buttons programmable to perform automatic sequence of defined actions.

              - Capable of deactivating select keypads to prevent accidental changes to light levels.

              - Buttons programmable for raise/lower of defined loads.

              - Buttons programmable to toggle defined loads on/off.

              - Status LED: LED illuminates upon being depressed and capable of logic-based status LED illumination based on scene, room, pathway, or last scene logic.

            - Mounting: Wallbox or low-voltage mounting bracket.

Retain "Button/Engraving Backlighting" Subparagraph below for Lutron's "seeTouch QS" or "Signature Series" keypads.

            - Button/Engraving Backlighting:

              - Use backlighting for buttons and associated engraving to allow readability in all lighting conditions.

              - Backlight intensity is programmatically adjustable.

            - Keypads with field-customizable button color.

Retain "Configurable Keypad" Subparagraph below for Lutron's "Architrave" or "Signature Series" keypads.

            - Configurable Keypad: Field-replaceable keys to customize configuration and engraving.

            - Contact Closure Interface: Two contact closure inputs on back of unit that provide independent functions from front buttons, customizable for momentary or maintained contact closure.

            - Terminal blocks to be overvoltage and miswire protected against wire reversals and short circuits.

        - Single-Scene or Zoned Wired Control:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; Pico Wired Control or comparable product by one of the following:

            - Cooper Industries, Inc.

            - Leviton Manufacturing Co., Inc.

            - <Insert manufacturer's name>.

          - Controls:

            - Turn an individual fixture or group of fixtures on and off.

            - Raise and lower light levels.

            - Recall favorite light levels.

        - Four-Button Preset Wired Wallstation:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; EcoSystem CC-4BRL Four-Button Control or comparable product by one of the following:

            - Cooper Industries, Inc.

            - Leviton Manufacturing Co., Inc.

            - <Insert manufacturer's name>.

          - Controls:

            - Recall four scenes plus all on or all off for one group of fixtures.

            - Master raise/lower control for entire group of fixtures.

            - Integral IR receiver for personal control.

            - Immediate local LED response upon button activation to indicate that a system command has been requested.

        - Wired Keyswitch:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; QS keyswitch or comparable product by one of the following:

            - Cooper Industries, Inc.

            - Leviton Manufacturing Co., Inc.

            - <Insert manufacturer's name>.

          - Configuration: [Three-position, momentary, center-position key removal] [Three-position, maintained, center-position key removal] [Two-position, maintained, center-position key removal] [Two-position, maintained, any-position key removal].

          - Allows control of any device connected to control.

          - Replacement of unit does not require reprogramming.

          - Communications: RS 485.

          - Requires key insertion to activate actions.

          - Engraved keypads with button, zone, and scene descriptions.

          - Software Configuration:

            - Key positions programmable to perform a single defined action.

            - Key positions programmable using conditional logic based on state variable such as time of day or partition status.

      - WIRELESS (RADIO FREQUENCY) CONTROLS

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; Pico Wireless Control or comparable product by one of the following:

          - Cooper Industries, Inc.

          - Leviton Manufacturing Co., Inc.

          - <Insert manufacturer's name>.

        - Features:

          - Configuration: [Two-button control] [Two-button control with nightlight] [Two button with raise/lower control] [Three-button control] [Three button with raise/lower control] [Three button with raise/lower control and nightlight] [Four button].

          - Communicates via radio frequency to compatible dimmers, switches, and plug-in modules.

          - No external power packs, power, or communication wiring.

          - Allows for easy reprogramming without replacing unit.

          - Button Programming:

            - Single action.

            - Toggle action.

            - Defined action on press and defined action on release.

          - Status LED to indicate button press or programming mode status.

          - Power: Battery operated with minimum 10-year battery life.

        - Accessories:

          - [Single] [Double] [Triple] [Quadruple] pedestal mount.

          - Surface mount.

          - Wallbox adapter, including faceplate with concealed hardware.

      - INFRARED HANDHELD CONTROLS

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; Model [C-FRLC-WH] [GRX-IT-WH] or comparable product by one of the following:

            - Cooper Industries, Inc.

            - Leviton Manufacturing Co., Inc.

            - <Insert manufacturer's name>.

Lutron's "Model GRX-IT-WH" infrared handheld control is capable of controlling one scene; "Model C-FRLC-WH" is capable of four-scene control.

          - Number of Scenes: [One] [Four].

Lutron's "Model GRX-IT-WH" infrared handheld control has a maximum range of 12 ft. (3.7 m); "Model C-FRLC-WH" has a maximum range of 50 ft. (15 m).

          - Range: [12 ft. (3.7 m)] [50 ft. (15 m)] line of sight.

          - Features:

            - Designed for use in conjunction with compatible infrared receiver and lighting control.

            - Learnable by other variable-frequency remote controls.

      - EMERGENCY LIGHTING INTERFACE

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Lutron Electronics Co., Inc.; Model LUT-ELI or comparable product by one of the following:

          - Cooper Industries, Inc.

          - Leviton Manufacturing Co., Inc.

          - <Insert manufacturer's name>.

        - Compliance: UL 924.

        - Features:

          - Senses all three phases of building power.

          - Provides output to power panels or digital ballast interfaces if power on any phase fails and sends all lights controlled by these devices to [emergency light level setting] [100 percent intensity].

          - Lights to return to previous intensities upon return of normal power.

          - Accepts a contact closure input from a fire alarm control panel.

      - FIELD-MOUNTED SIGNAL SOURCES

        - Daylight Harvesting Switching Controls: Comply with Section 260923 "Lighting Control Devices." Control power may be taken from the lighting control panel, and signal must be compatible with the relays.

        - Indoor Occupancy Sensors[ and Extreme-Temperature Occupancy Sensors]: Comply with Section 260923 "Lighting Control Devices." Control power may be taken from the lighting control panel, and signal must be compatible with the relays.

      - CONDUCTORS AND CABLES

        - Power Wiring to Supply Side of Class 2 Power Source: Not smaller than No. 12 AWG. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Classes 2 and 3 Control Cables: Multiconductor cable with copper conductors not smaller than [No. 18] [No. 22] [No. 24] AWG. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Class 1 Control Cables: Multiconductor cable with copper conductors not smaller than [No. 14] [No. 16] [No. 18] AWG. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Twisted-Pair Data Cable: [Category 5e] [Category 6] [Category 6a].

Retain one of two subparagraphs below.

          - Comply with requirements for twisted pair cabling in Section 260523 "Control-Voltage Electrical Power Cables."

          - Comply with requirements in Section 271513 "Communications Copper Horizontal Cabling."

- EXECUTION

      - EXAMINATION

        - Receive, inspect, handle, and store panels in accordance with NECA 407.

        - Examine panels before installation. Reject panels that are damaged or rusted or have been subjected to water saturation.

        - Examine elements and surfaces to receive panels for compliance with installation tolerances and other conditions affecting performance of the Work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION OF WIRING

        - Wiring Methods:

Retain one of first three subparagraphs below.

          - Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters.

          - Install cables in raceways and cable trays except within consoles, cabinets, desks, counters, accessible ceiling spaces, and gypsum board partitions where unenclosed wiring method may be used.

          - Install conductors and cables concealed in accessible ceilings, walls, and floors where possible.

          - Conceal raceway and cables except in unfinished spaces.

          - Provide plenum-rated cable, where installed exposed or in open cable tray, within environmental airspaces, including plenum ceilings.

          - Comply with requirements for cable trays specified in Section 260536 "Cable Trays for Electrical Systems."

          - Comply with requirements for raceways and boxes specified in Section 260533 "Raceways and Boxes for Electrical Systems."

        - Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

      - INSTALLATION OF PANELS

        - Install panels and accessories in accordance with NECA 407.

Retain first paragraph below if seismic controls are required for Project. Coordinate with Drawings.

        - Comply with mounting and anchoring requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

When specifying height for top of trim in first paragraph below, make sure the center of the grip of all operating handles or circuit breakers, when in their highest position, is not higher than 79 inch (2000 mm) above finished floor or grade.

        - Mount top of trim [90 inch (2286 mm)] <Insert dimension> above finished floor unless otherwise indicated.

        - Mount panel cabinet plumb and rigid without distortion of box.

        - Install filler plates in unused spaces.

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

        - Identify field-installed conductors, interconnecting wiring, and components; provide warning signs complying with Section 260553 "Identification for Electrical Systems."

        - Create a directory to indicate loads served by each relay; incorporate Owner's final room designations. Obtain approval before installing. Use a PC or typewriter to create directory; handwritten directories are unacceptable.

        - Lighting Control Panel Nameplates: Label each panel with a nameplate complying with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

      - FIELD QUALITY CONTROL

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

Coordinate "Tests and Inspections" Paragraph below with "Qualifications" and "Field Quality Control" articles in Section 260010 "Supplemental Requirements for Electrical."

        - Tests and Inspections:

Retain option in first subparagraph below if panelboards with factory-installed SPD are specified.

List of tests is from that stated in NETA ATS, Paragraph 7.6, "Circuit Breakers," and Paragraph 7.19.1, "Surge Arrestors, Low-Voltage." Coordinate tests and test values with testing agency and manufacturer.

          - Perform each visual and mechanical inspection and electrical test for low-voltage air circuit breakers described below[ and low-voltage surge arrestors]. Certify compliance with manufacturer's test parameters.

            - Circuit-Breaker Tests:

              - Compare nameplate with Drawings and Specifications.

              - Inspect physical and mechanical conditions.

              - Inspect anchorage and alignment.

              - Verify that the units are clean.

              - Operate the circuit breaker to ensure smooth operation.

              - Inspect bolted electrical connections for high resistance using one or more of the following methods:

                - A low-resistance ohmmeter.

                - Verify tightness of bolted electrical connections by calibrated torque wrench.

                - Thermographic survey.

              - Inspect operating mechanism, contacts, and arc chutes in unsealed units.

              - Perform adjustments for final protective device settings in accordance with the overcurrent protective device coordination study. Comply with requirements in Section 260573.16 "Coordination Studies."

              - Perform insulation resistance tests for one minute on each pole, phase-to-phase, and phase-to-ground with the circuit breaker closed and across each pole using manufacturer's published data.

              - Perform a contact/pole-resistance test.

              - Perform insulation-resistance tests on control wiring with respect to ground. Applied potential shall be 500 V(dc) for 300 V rated cable and 1000 V(dc) for 600 V rated cable. Test duration shall be for one minute. Follow manufacturer's instructions for solid-state units.

              - Determine long-time pickup and delay by primary current injection.

              - Determine short-time pickup and delay by primary current injection.

              - Determine ground-fault pickup and time delay by primary current injection.

              - Determine instantaneous pickup by primary current injection.

              - Test functions of the trip unit by means of secondary injection.

              - Perform minimum pickup voltage tests on shunt trip and close coils in accordance with manufacturer's published data.

              - Verify correct operation of auxiliary features such as trip and pickup indicators, zone interlocking, electrical close and trip operation, trip-free, anti-pump function, and trip unit battery condition. Reset trip logs and indicators.

              - Verify operation of charging mechanism.

Retain "Surge Arrestor Tests" Subparagraph below if retaining low-voltage surge arrestors above.

            - Surge Arrestor Tests:

              - Compare nameplate with the Contract Documents.

              - Inspect physical and mechanical conditions.

              - Inspect anchorage, alignment, grounding, and clearances.

              - Verify that the units are clean.

              - Inspect bolted electrical connections for high resistance using one or more of the following methods:

                - Low-resistance ohmmeter.

                - Verify tightness of bolted electrical connections by calibrated torque wrench.

              - Verify that the ground lead on each device is individually attached to a ground bus or ground electrode.

              - Perform an insulation-resistance test on each arrestor, phase terminal-to-ground using voltage in accordance with manufacturer instructions.

              - Comply with requirements in Section 260526 "Grounding and Bonding for Electrical Systems" for grounding tests.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Lighting control panel will be considered defective if it does not pass tests and inspections.

          - Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

Retain first paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

        - Prepare test and inspection reports, including a certified report that identifies lighting control panels and describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations made after remedial action.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 260010 "Supplemental Requirements for Electrical" for field tests and inspections.

        - Manufacturer Services:

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks in accordance with manufacturer's instructions.

          - Confirm correct communications wiring, initiate communications between panels, and program the lighting control system in accordance with approved configuration schedules, time-of-day schedules, and input override assignments.

          - <Insert startup steps if any>.

      - ADJUSTING

        - Occupancy Adjustments: When requested within [12] <Insert number> months from date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

      - MAINTENANCE

        - Software and Firmware Service Agreement:

Services in this article may not be allowed for publicly funded projects.

          - Technical Support: Beginning at Substantial Completion, verify that software and firmware service agreement includes software support for [two] <Insert number> years.

          - Upgrade Service: At Substantial Completion, update software and firmware to latest version. Install and program software upgrades that become available within [two] <Insert number> years from date of Substantial Completion. Verify upgrading software includes operating system and new or revised licenses for using software.

            - Upgrade Notice: No fewer than [30] <Insert number> days to allow Owner to schedule and access the system and to upgrade computer equipment if necessary.

          - Upgrade Reports: Prepare written report after each update, documenting upgrades installed.

END OF SECTION 260943.23