SECTION 260943

NETWORK LIGHTING CONTROLS - LUTRON HOMEWORKS

This section includes network-connected lighting controls featuring basis of design products from Lutron Electronics Company, Inc. Because of the complex nature of this type of system, it is recommended that the specification and drawings be closely coordinated with consultation from the basis of design manufacturer. If systems of other manufacturers are listed or considered for substitution, the specifier should conduct a thorough evaluation to ensure that the system provides equivalent performance and that other related products will interface properly.

SECTION 26 0943 (16575) - NETWORK LIGHTING CONTROLS – LUTRON HOMEWORKS, Copyright 2011-2024, Lutron Electronics Company, Inc.

- GENERAL

  - SECTION INCLUDES

    - Lighting control system and associated components:

      - LED drivers.

      - Power interfaces.

      - Lighting control system processor.

      - Centralized lighting control system software.

      - Cloud services interface.

      - Radio frequency (RF) repeaters.

      - Control stations.

      - Wall dimmers, switches, and fan speed controllers.

      - Load control modules.

      - Low-voltage control interfaces.

      - HVAC controls by Lighting Control Manufacturer, for system control interface.

      - Wired sensors.

      - Wireless sensors.

      - Accessories.

  - RELATED REQUIREMENTS

Include the following paragraph only if motorized shades are to be controlled by the lighting control system.

    - Section 12 2400 - <<Window Shades – Lutron Sivoia QS/Sivoia QS Wireless; Window Shades – Lutron Serena/Triathlon; Window Shades – Lutron Contract Roller >>:  Motorized roller window shades, for interface with lighting control system.

    - Section 26 0553 - Identification for Electrical Systems:  Identification products and requirements.

    - Section 26 2726 - Wiring Devices - Lutron:

      - Finish requirements for wall controls specified in this section.

      - Accessory receptacles and wall plates, to match lighting controls specified in this section.

    - Section 26 5133 - Luminaires, Ballasts, and Drivers - Lutron.

    - Section 26 5134 - Luminaires, Lamps, and Accessories – Ketra:  Residential line tunable LED luminaires/lamps and accessory controls/interfaces, for interface with lighting control system.

    - Section <<______>>:  Audio-video system, for interface with lighting control system.

  - REFERENCE STANDARDS

    - 47 CFR 15 - Radio Frequency Devices; current edition.

    - ANSI C82.11 - American National Standard for Lamp Ballasts - High Frequency Fluorescent Lamp Ballasts - Supplements; 2023.

    - ANSI C137.1 – Lighting Systems – 0-10V Dimming Interface for LED Drivers, Fluorescent Ballasts, and Controls; 2022.

    - ANSI/ESD S20.20 - Protection of Electrical and Electronic Parts, Assemblies and Equipment (Excluding Electrically Initiated Explosive Devices); 2021.

    - ASTM D4674 - Standard Practice for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Office Environments; 2019.

    - ASTM E308 - Standard Practice for Computing the Colors of Objects by Using the CIE System; 2022.

    - CAL TITLE 24 P6 – California Code of Regulations, Title 24, Part 6 (California Energy Code); 2022.

    - CSA C22.2 No. 223 – Power Supplies with Extra-low-voltage Class 2 Outputs; 2015 (Reaffirmed 2020).

    - IEC 60529 – Degrees of Protection Provided by Enclosures (IP Code); 2013 (Corrigendum 2019).

    - IEC 60669-2-1 - Switches for Household and Similar Fixed Electrical Installations - Part 2-1: Particular Requirements - Electronic Switches; 2021.

    - IEC 60929 - AC and/or DC-Supplied Electronic Control Gear for Tubular Fluorescent Lamps - Performance Requirements; 2011, with Amendment (2015).

    - IEC 61000-4-2 - Electromagnetic Compatibility (EMC) - Part 4-2: Testing and Measurement Techniques - Electrostatic Discharge Immunity Test; 2008.

    - IEC 61000-4-5 - Electromagnetic Compatibility (EMC) - Part 4-5: Testing and Measurement Techniques - Surge Immunity Test; 2014, with Amendment (2017).

    - IEC 61347-2-3 - Lamp Control Gear - Part 2-3: Particular Requirements for A.C. and/or D.C. Supplied Electronic Control Gear for Fluorescent Lamps; 2011, with Amendments, 2016

    - IEEE 1789 - Recommended Practice for Modulating Current in High-Brightness LEDs for Mitigating Health Risks to Viewers; 2015.

    - IEEE C62.41.2 - Recommended Practice on Characterization of Surges in Low-Voltage (1000 V and less) AC Power Circuits; 2002 (Corrigendum 2012).

    - ISO 9001 - Quality Management Systems-Requirements; 2015.

    - NECA 1 - Standard for Good Workmanship in Electrical Construction; 2015.

    - NECA 130 - Standard for Installing and Maintaining Wiring Devices; National Electrical Contractors Association; 2016.

    - NEMA 410 - Performance Testing for Lighting Controls and Switching Devices with Electronic Drivers and Discharge Ballasts; National Electrical Manufacturers Association; 2020.

    - NEMA SSL 7A – Phase Cut Dimming for Solid State Lighting: Basic Compatibility; 2015 (Reaffirmed 2021).

    - NEMA WD 1 - General Color Requirements for Wiring Devices; National Electrical Manufacturers Association; 1999 (Reaffirmed 2020).

    - NFPA 70 - National Electrical Code; National Fire Protection Association; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.

    - UL 20 - General-Use Snap Switches; Current Edition, Including All Revisions.

    - UL 94 - Tests for Flammability of Plastic Materials for Parts in Devices and Appliances; Current Edition, Including All Revisions.

    - UL 489 - Molded-Case Circuit Breakers, Molded-Case Switches and Circuit Breaker Enclosures; Current Edition, Including All Revisions.

    - UL 508 - Industrial Control Equipment; Current Edition, Including All Revisions.

    - UL 1310 – Class 2 Power Units; Current Edition, Including All Revisions.

    - UL 1472 - Solid-State Dimming Controls; Current Edition, Including All Revisions.

    - UL 1598C - Light-Emitting Diode (LED) Retrofit Luminaire Conversion Kits; Current Edition, Including All Revisions.

    - UL 2043 - Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces; Current Edition, Including All Revisions.

    - UL 8750 - Light Emitting Diode (LED) Equipment for Use in Lighting Products; Current Edition, Including All Revisions.

  - ADMINISTRATIVE REQUIREMENTS

    - Coordination:

      - Coordinate the placement of sensors and wall controls with millwork, furniture, equipment, etc. installed under other sections or by others.

      - Coordinate the placement of wall controls with actual installed door swings.

      - Coordinate the placement of daylight sensors with windows, skylights, and luminaires to achieve optimum operation. Coordinate placement with ductwork, piping, equipment, or other potential obstructions to light level measurement installed under other sections or by others.

Include the following paragraph only if motorized shades are to be controlled by the lighting control system.

      - Where motorized window treatments are to be controlled by the lighting control system provided under this section, coordinate the work with other trades to provide compatible products.

      - Coordinate the work to provide luminaires and lamps compatible with the lighting controls to be installed.

      - Notify Architect and Lighting Designer of any conflicts or deviations from the contract documents to obtain direction prior to proceeding with work.

    - Preinstallation Meeting:  Conduct on-site meeting with Residential System Provider prior to commencing work to review:

      - Low voltage wiring requirements.

      - Separation of power and low voltage/data wiring.

      - Wire labeling.

      - HomeWorks Processor locations and installation.

      - Control locations.

      - Load circuit wiring.

      - Network wiring requirements.

      - Connections to other equipment.

      - Installer responsibilities.

      - Control of nonlighting loads (e.g., fans, motorized doors, storm shutters).

    - Sequencing:

      - Do not install sensors and wall controls until final surface finishes << and painting>> are complete.

  - SUBMITTALS

    - See Section 01 3000 - Administrative Requirements for submittal procedures.

    - Product Data:  Include ratings, configurations, standard wiring diagrams, dimensions, colors, service condition requirements, and installed features.

      - Occupancy/Vacancy Sensors:  Include detailed motion detection coverage range diagrams.

    - Shop Drawings:

      - Provide load schedule indicating actual connected load, load type, and voltage per circuit, circuits and their respective control zones, circuits that are on emergency, and capacity, phase, and corresponding circuit numbers.

      - Provide schematic system riser diagram indicating component interconnections. Include requirements for interface with other systems.

    - Samples:

      - Wall Controls:

        - Show available color and finish selections.

        - Provide <<one; or _____>> sample(s) for each product << proposed for substitution; or __________>><< upon request; or __________>>.

      - Sensors:  Provide <<one; or _____>> sample(s) for each product << proposed for substitution; or __________>><< upon request; or __________>>.

    - Manufacturer's Installation Instructions:  Include application conditions and limitations of use stipulated by product testing agency. Include instructions for storage, handling, protection, examination, preparation, and installation of product.

Include the following paragraph if lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) is specified in Part 3 under "COMMISSIONING".

    - Title 24 Acceptance Testing Documentation:  Submit Certification of Acceptance and associated documentation for lighting control acceptance testing performed in accordance with CAL TITLE 24 P6, as specified in Part 3 under “COMMISSIONING”.

    - Project Record Documents:  Record actual installed locations and settings for lighting control system components.

    - Operation and Maintenance Data:  Include detailed information on lighting control system operation, equipment programming and setup, replacement parts, and recommended maintenance procedures and intervals.

- Residential Systems Provider to provide sequence of operations overview for programming that will be executed by keypads, timeclock events, etc.

  - Keypads start as programmed with brightest scenes at top and off at bottom.

  - Keypads to start as Palladiom Keypads with 4-button configuration.

- Residential Systems Provider to provide overview of servicing plans of lighting control system components and programming.

- Residential Systems Provider to provide keypad engraving proposal.

  - Engrave all keypads.

  - Residential Systems Provider to provide plan for timing and execution of final keypad engraving based upon project timeline and final styles of keypads selected.

    - Warranty: Submit sample of manufacturer's Warranty as specified in Part 1 under "WARRANTY". Submit documentation of final execution completed in Owner's name and registered with manufacturer.

  - QUALITY ASSURANCE

    - Conform to requirements of NFPA 70.

    - Maintain at the project site a copy of each referenced document that prescribes execution requirements.

    - Manufacturer Qualifications:

      - Company with not less than ten years of experience manufacturing lighting control systems of similar complexity to specified system.

      - Registered to ISO 9001, including in-house engineering for product design activities.

      - Qualified to supply specified products and to honor claims against product presented in accordance with warranty.

Include the following paragraph if lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) is specified in Part 3 under "COMMISSIONING".

    - Title 24 Acceptance Testing Technician Qualifications:  Certified by a California approved Acceptance Test Technician Certification Provider as an Acceptance Test Technician (ATT) in accordance with CAL TITLE 24 P6.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in a clean, dry space in original manufacturer's packaging in accordance with manufacturer's written instructions until ready for installation.

  - FIELD CONDITIONS

    - Maintain field conditions within manufacturer's required service conditions during and after installation.

      - Basis of Design System Requirements - Lutron, Unless Otherwise Indicated:

        - Ambient Temperature:

          - Lighting Control System Components, Except Those Listed Below:  Between 32 and 104 degrees F (0 and 40 degrees C).

        - Relative Humidity:  Less than 90 percent, non-condensing.

During the installation phase, considerable dust (drywall, concrete, etc) may be deposited on electrical components and impair performance. General accepted housekeeping protection of the electrical equipment must be maintained.

        - Protect against accumulation or infiltration of dust.

  - WARRANTY

    - See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

    - Manufacturer’s Standard Warranty:

      - Manufacturer Lighting Control System Components, Except Wireless Sensors and LED Drivers:

        - First Two Years:  100 percent replacement parts coverage, no manufacturer labor coverage.

        - Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

      - Wireless Sensors:  Five years 100 percent parts coverage, no manufacturer labor coverage.

      - LED Drivers:  Three years 100 percent parts coverage, no manufacturer labor coverage.

- PRODUCTS

  - MANUFACTURERS

    - Basis of Design Manufacturer:  Lutron Electronics Company, Inc; HomeWorks; www.lutron.com.

    - Other Acceptable Manufacturers:

      - <<______>>.

      - Products by listed manufacturers are subject to compliance with specified requirements<< and prior approval of Architect; or _________>>.

    - Substitutions:  <<See Section 01 6000 - Product Requirements; Not permitted; or __________>>.

Delete the following three subparagraphs if substitutions are not permitted.

      - All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by Architect a minimum of <<10; or _____>> working days prior to the bid date and must be made available to all bidders. Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

      - By using pre-approved substitutions, Contractor accepts responsibility and associated costs for all required modifications to related equipment and wiring. Provide complete engineered shop drawings (including power wiring) with deviations from the original design highlighted in an alternate color for review and approval by Architect prior to rough-in.

  - LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS

    - Provide products listed, classified, and labeled by Underwriter's Laboratories Inc. (UL) as suitable for the purpose indicated.

    - Unless specifically indicated to be excluded, provide all required equipment, conduit, boxes, wiring, connectors, hardware, supports, accessories, software, system programming, etc. as necessary for a complete operating system that provides the control intent indicated.

Only include the following paragraph if motorized shades are to be controlled by the lighting control system.

    - Shade Control Requirements:

      - Capable of operating shades and recalling shade presets via keypad, contact closure input, infrared receiver, lighting management system software, or other lighting control system interface.

      - Capable of operating any individual, group, or subgroup of shade electronic drive units within system without requiring separate group controllers.

      - Capable of assigning and reassigning individual, groups, and subgroups of shades to any control within system without requiring additional wiring or hardware changes.

      - Capable of controlling shade speed for tracking within plus or minus 0.125 inch (3.17 mm) throughout entire travel.

      - Provide 10 year power failure memory for preset stops, open and close limits, shade grouping and sub grouping and system configuration.

      - Capable of synchronizing multiple shade electronic drive units of the same size to start, stop and move in unison.

      - Capable of stopping shades within accuracy of 0.125 inch (3.17 mm) at any point between open and close limits.

      - Capable of storing up to 250 programmable stop points, including open, close, and any other position.

      - Capable of controlling lights and shades from single wall control button.

Typical dimming equipment is rated for 40 degrees C (104 degrees F). This is the maximum ambient temperature that can exist while the dimming equipment is operating at full load conditions. Include the following paragraph to ensure that the operating equipment is designed to operate at worst case environmental conditions without affecting product life.

    - Design lighting control equipment for 10 year operational life while operating continually at any temperature in an ambient temperature range of 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C) and 90 percent non-condensing relative humidity.

Electrostatic charge builds up on people as a result of friction (walking across a carpet). When a person touches an electronic device, a discharge can occur and cause damage. Electrostatic discharge (ESD) testing is done according to the IEC 61000-4-2 standard (human body model). Testing should be completed on all user accessible points such as terminal blocks, buttons, and control inputs. The standard only describes how to conduct the test, which is why it is important to specify "without impairment of performance" as the pass/fail criteria.

    - Electrostatic Discharge Tolerance: Design and test equipment to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

    - Dimming and Switching (Relay) Equipment:

Electrolytic capacitors are typically the component most sensitive to heat in a dimming circuit. Their expected lifetime doubles for every 10 degrees C that the component operates below the capacitor's rated operating temperature so a capacitor operated at 20 degrees C below the rated temperature will have quadruple the life expectancy. Include the following paragraph to ensure a minimum 10 year operating life under worst case field conditions.

      - Designed so that electrolytic capacitors operate at least 36 degrees F (20 degrees C) below the capacitor's maximum temperature rating when the device is under fully loaded conditions at maximum rated temperature.

Dimming equipment is exposed to peak currents much higher than rated operating current due to tungsten inrush, magnetic inrush, and lamp burnout. If not designed to handle this inrush/surge condition, the equipment could fail at any time when turned on or when lamps fail. Include the following paragraph to ensure reliability of components.

      - Inrush Tolerance:

        - Utilize load-handling thyristors (SCRs and triacs), field effect transistors (FETs) and isolated gate bipolar transistors (IGBTs) with maximum current rating at least two times the rated operating current of the dimmer/relay.

        - Capable of withstanding repetitive inrush current of 50 times the operating current without impacting lifetime of the dimmer/relay.

A surge protector is sold as an accessory to a computer purchase to protect it from lightning strikes or other voltage surges. Likewise, dimmer circuits require surge protection. Surge protection can be built into a dimmer circuit or it can be purchased separately as an external accessory. Include the following paragraph to ensure that the surge protection is built into the dimming system.

      - Surge Tolerance:

Power handling devices installed on a branch circuit (far from electrical service entrance points) need to survive a Category A near lightning strike without failure. The standard only describe testing, which is why it is important to specify "without impairment to performance" as the pass/fail criteria.

        - Power Handling Devices: Designed and tested to withstand surges of 6,000 V, 200 amps according to IEEE C62.41.2 without impairment to performance.

Power dropouts occur frequently. When power is restored, the lighting system should recover quickly and automatically return to the last lighting levels. A momentary interruption (1 or 2 seconds) of power should not cause extended periods (20 seconds or more) without lighting while the system reboots and all other electrical equipment is back on.

      - Power Failure Recovery: When power is interrupted and subsequently restored, within 3 seconds lights to automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

      - Dimming Requirements:

Utility power is subject to many sources of line noise. Dimming equipment must maintain constant light levels in the presence of this line noise.

        - Line Noise Tolerance: Provide real-time cycle-by-cycle compensation for incoming line voltage variations including changes in RMS voltage (plus or minus 2 percent change in RMS voltage per cycle), frequency shifts (plus or minus 2 Hz change in frequency per second), dynamic harmonics, and line noise.

          - Systems not providing integral cycle-by-cycle compensation to include external power conditioning equipment as part of dimming system.

Include this paragraph to minimize surge currents and extend lamp life.

        - Incorporate electronic "soft-start" default at initial turn-on that smoothly ramps lights up to the appropriate levels within 0.5 seconds.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock. It is common for this leakage current to exceed 5 milliamps (the UL limit for GFCI outlets). Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

        - Utilize air gap off to disconnect the load from line supply.

Digital control systems have a fixed number of steps in their light control output. There needs to be enough steps to ensure the human eye perceives smooth changes when moving from one light level to another.

        - Control all light sources in smooth and continuous manner. Dimmers with visible steps are not acceptable.

Different lighting sources such as fluorescent and incandescent require different power levels to dim from minimum to maximum. Dimmers with too narrow a control range will not give the full dimming performance. Dimmers with too broad a control range will have areas where changing the dimmers light level will not result in a change in light output. Dimmers must be flexible enough to compensate for these different load types.

        - Load Types:

          - Assign a load type to each dimmer that will provide a proper dimming curve for the specific light source to be controlled.

          - Provide capability of being field-configured to have load types assigned per circuit.

Variations in lamp and fixture designs may require fine tuning of dimming curves. Include this paragraph to ensure the equipment has the capability to make these adjustments. This also allows facility personnel to manage maximum light levels to achieve energy savings goals.

        - Minimum and Maximum Light Levels: User adjustable on a circuit-by-circuit basis.

        - Line Voltage Dimmers:

Magnetic transformers are susceptible to overheating caused by asymmetrical input voltages. Include the following paragraphs to prevent magnetic low voltage transformers from operating above rated current and temperature under normal conditions or component failure.

          - Dimmers for Magnetic Low Voltage (MLV) Transformers:

            - Provide circuitry designed to control and provide a symmetrical AC waveform to input of magnetic low voltage transformers per UL 1472.

            - Dimmers using unipolar load current devices (such as FETs or SCRs) to include DC current protection in the event of a single device failure.

Electronic transformers are susceptible to damage and audible noise issues if used with improper dimming waveforms. Most electronic transformers require a reverse phase control waveform. Transformer manufacturers should be able to provide detailed information on dimming requirements.

          - Dimmers for Electronic Low Voltage (ELV) Transformers: Operate transformers via reverse phase control. Alternately, forward phase control dimming may be used if dimming equipment manufacturer has recommended specific ELV transformers being provided.

          - Dimmers for Neon and Cold Cathode Transformers:

There are both high power factor and low power factor transformers. Dimming is only applicable on the low power factor transformers. Attempting to dim high power factor transformers can damage both the transformer and dimmer, and generate electrical noise on building's electrical supply that interferes with other equipment.

            - Magnetic Transformers: Listed for use with normal (low) power factor magnetic transformers.

Electronic transformer technology is continually evolving. At this time Lutron does not recommend any electronic neon transformers for dimming applications. Lutron continues to evaluate products as they become available on the market. Please consult with your Lutron representative for the latest technologies.

            - Electronic Transformers: Must be supported by the ballast equipment manufacturer for control of specific ballasts being provided.

        - Low Voltage Dimming Modules:

Some electronic dimming ballasts require:

-A switching circuit to apply or remove power to/from the ballast.

-A low voltage control signal for intensity information.

Dimming control must coordinate both of these items.

          - Coordination Between Low Voltage Dimming Module and Line Voltage Relay:  Capable of being electronically linked to a single zone.

IEC 60929 is a standard for electronic fluorescent ballasts, and is used by other lighting equipment controlled by low voltage signals including LED drivers and low voltage controlled neon. It defines specific methods for 0-10V, pulse width modulation (PWM), and Digitally Addressable Lighting Interface (DALI).

          - Single low voltage dimming module; capable of controlling the following light sources:

            - 0-10V analog voltage signal.

              - Provide Class 2 isolated 0-10V output signal conforming to IEC 60929.

              - Sink current according to IEC 60929.

              - Source current.

            - 10-0V reverse analog voltage signal.

Lutron Softswitch circuitry prevents arcing at the relay contacts for all three load types, and extends the relay life in excess of one million cycles. Switching high inrush loads can damage relay controls over time. The arcing of these relays, depending on load, typically will limit relay life to 10,000 or 50,000 cycles.

      - Switching Requirements:

        - Rated Life of Relays: Typical of 1,000,000 cycles at fully rated 16 A for all lighting loads.

        - Switch load in a manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

        - Provide output fully rated for continuous duty for inductive, capacitive, and resistive loads.

    - Device Finishes:

      - Wall Controls: <<Match finishes specified for wiring devices in Section 26 2726, unless otherwise indicated; As indicated on the drawings; To be selected by Architect; or __________>>.

      - Standard Colors: Comply with NEMA WD1 where applicable.

      - Color Variation in Same Product Family: Maximum delta E of 1, CIE L*a*b color units per ASTM E308.

Daylight or fluorescent lighting generate ultraviolet light which can cause parts that do not meet ASTM D4674 to discolor/yellow over time.

      - Visible Parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

    - Interface with Existing Work: <<______>>.

  - LED DRIVERS

    - General Requirements:

Include the following paragraph to ensure that the driver is designed to operate at worst case environmental conditions without affecting product life.

      - Operate for at least 50,000 hours at maximum case temperature and 90 percent non-condensing relative humidity.

      - Provide thermal fold-back protection by automatically reducing power output (dimming) to protect LED driver and LED light engine/fixture from damage due to over-temperature conditions that approach or exceed the LED driver's maximum operating temperature at calibration point.

      - Provide integral recording of operating hours and maximum operating temperature to aid in troubleshooting and warranty claims.

Electrostatic charge builds up on people as a result of friction (walking across a carpet). When a person touches an electronic device, a discharge can occur and cause damage. Electrostatic discharge (ESD) testing is done according to the IEC 61000-4-2 standard (human body model). Testing should be completed on all user accessible points such as terminal blocks, buttons, and control inputs. The standard only describes how to conduct the test, which is why it is important to specify "without impairment of performance" as the pass/fail criteria.

      - Designed and tested to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

During manufacturing, ballasts are more susceptible to damage by electrostatic discharge (ESD). A facility that does not meet this requirement could have excessive defective units delivered to a job site.

      - Manufactured in a facility that employs ESD reduction practices in compliance with ANSI/ESD S20.20.

UL 8750 is a UL safety standard that covers LED drivers.

      - UL 8750 recognized or listed as applicable.

UL Type TL and UL Class P are UL ratings for an LED driver. LED drivers that are Type TL rated can be easily swapped in a fixture by the fixture manufacturer with lower re-testing time and certification cost. LED drivers that are Class P listed can be swapped without any re-testing time or certification cost.

      - UL Type TL rated or UL Class P listed where possible to allow for easier fixture evaluation and listing of different driver series.

If a driver needs to be replaced in the field, a UL recognized driver listed for field replacement under UL 1598C can be replaced with a like driver. Without a UL 1598C rating, you will either have to send the fixture back to the manufacturer or have UL re-inspect the fixture in the field. UL listed Class P drivers are also suitable for field replacement.

      - Suitable for field replacement as applicable; listed in accordance with UL 1598C or UL 8750, Class P as indicated.

A surge protector is sold as an accessory to a computer purchase to protect it from lightning strikes or other voltage surges. Likewise, dimmer circuit require surge protection. Surge protection can be built into a driver or it can be purchased separately as an external accessory. Include the following paragraph to ensure that the surge protection is built into the drivers.

      - Designed and tested to withstand Category A surges of 4,000 V according to IEEE C62.41.2 without impairment of performance.

The following means that the driver will be inaudible in a general office space (30dBA is a quiet whisper at 5 feet).

      - Class A sound rating; Inaudible in a 27 dBA ambient.

Line voltage fluctuates throughout the day as equipment (i.e. equipment or other buildings in the vicinity) come on line. Line voltage fluctuations will cause noticeable changes in light output. The driver automatically compensates for variations in voltage to provide constant light output.

      - Demonstrate no visible change in light output with a variation of plus or minus 10 percent change in line-voltage input.

      - LED drivers of the same family/series to track evenly across multiple fixtures at all light levels.

To meet the lighting density requirements of a job, the fixture OEM needs to deliver fixtures with custom lumen output levels. Programmable LED drivers allow the OEM to easily customize their fixtures. Full dimming range 100%-5% or 100%-1% must be achieved at any programmed level.

      - Offer low-end dimming range of 100 to 0.1 percent, 100 to 1 percent or 100 to 5 percent as applicable.

The following paragraph ensures that electronic dimming drivers will meet NEMA inrush recommendations, reducing false circuit breaker tripping due to turn on inrush. NEMA 410 defines the worst case inrush current expected to be encountered in field installations, and establishes uniform testing criteria for compatibility between controls, ballasts, drivers, etc.

      - Meet NEMA 410 inrush requirements for mitigating inrush currents with solid state lighting sources.

LED drivers with fault protection ensure that a wiring mistake that results in up to 277 V being applied to the communication links on the driver will not damage the driver and require the fixture to be replaced at significant cost.

      - Employ integral fault protection up to 277 V to prevent LED driver damage or failure in the event of incorrect application of line-voltage to communication link inputs.

Sometimes, the driver cannot be installed within the fixture, e.g. a chandelier. A driver that is remote mountable allows you to place the driver in a convenient location, without affecting the dimming performance of the driver.

      - LED driver may be remote located up to 100 feet (30 m) from LED light engine depending on power outputs required and wire gauge utilized by installer.

Lutron's EcoSystem® is a commercial lighting control system that is comprised of digitally addressable dimming ballasts, controls, and environmental sensors. These components provide businesses with energy savings from 40 to 70%, while increasing space flexibility, improving occupant comfort and productivity, and reducing maintenance costs.

    - Digital Control (when used with compatible Lutron lighting control systems):

After a power interruption, the lights in the space should go back to where they were prior to the interruption without flashing to full, or requiring a manual intervention. Power failure memory prevents annoying interruption to work after a power interruption.

      - Employ power failure memory; LED driver to automatically return to the previous state/light level upon restoration of utility power.

      - Operate from input voltage of 120 V through 277 V at 50/60 Hz.

      - Automatically go to 100 percent light output upon loss of control link voltage and lock out system commands until digital control link voltage is restored.

Conventional load shedding systems can be limited in their performance when the load shedding signal is sent to a dimmed circuit. For example, if a 10 percent load shedding command is sent to a circuit dimmed at 80 percent, the circuit would not respond to the command because it is already operating below the limit set by the load shedding command.

      - Responds to digital load shed command. (Example: If light output is at 30 percent and a load shed command of 10 percent is received, the LED driver automatically sets the maximum light output at 90 percent and lowers current light output by three percent to 27 percent).

To simplify wiring, EcoSystem digital low voltage control wiring is able to be wired as either class 1 or class 2. Class 1 wiring allows the wiring to share a conduit with power wiring (where allowed by local codes) and reduce the cost of pulling control wiring in the ceiling.

      - Digital low-voltage control wiring capable of being wired as either Class 1 or Class 2.

    - Product(s):

HomeWorks Digital 0.1% Constant Voltage LHD0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - Digital Control, 0.1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance; Lutron HomeWorks Digital 0.1% Constant Voltage (LHD0-Series):

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black (Lutron Soft-On, Fade-to-Black™) low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates 0.25 W standby power at 120 V and 0.40 W standby power at 277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at maximum power; complies with ANSI C82.11.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected, open circuit protected, and overload protected.

        - Constant Voltage Drivers:

          - Support for cove and under-cabinet fixtures at 24 V.

            - Support LED arrays from 2 W to 96 W.

IEEE 1789 sets the minimum frequency for PWM dimming above 1250 Hz to reduce chances for any disturbance in video recording.

            - Pulse Width Modulation (PWM) dimming frequency meets IEEE 1789.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

HomeWorks Digital 0.1% Constant Current PHQ0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - Digital Control, 0.1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance; Lutron HomeWorks Digital 0.1% Constant Current (PHQ0-Series):

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black (Lutron Soft-On, Fade-to-Black™) low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates less than 0.5 W standby power at 120/277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120/277 V.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected and open circuit protected.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

HomeWorks Digital 1% (PHQ1 Series) LED Drivers provide a high-performance solution for any space, in any application, while providing smooth, continuous dimming down to 1 percent of output current.

      - Digital Control, 1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance; Lutron HomeWorks Digital 1% Constant Current (PHQ1-Series):

        - Dimming Range:  100 to 1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black (Lutron Soft-On, Fade-to-Black™) low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates less than 0.5 W standby power at 120/277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120/277 V.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected and open circuit protected.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

Hi-lume® 1% (LTE-Series) Driver is a high-performance LED driver that provides smooth, continuous 1% dimming for virtually any LED fixture, whether it requires constant current or constant voltage. It is the most versatile LED driver offered today due to its compatibility with a wide variety of LED arrays, multiple form factors, and numerous control options.

      - Forward Phase (Neutral Wire Required), One Percent Dimming; Lutron Hi-lume 1% (LTE-Series):

        - Dimming Range:  100 to one percent relative light output.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at full output for 40 W loads; complies with ANSI C82.11.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 53 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for cove and under-cabinet fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

        - Constant Voltage Drivers:

          - Support for downlights and pendant fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for cove and under-cabinet fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

  - POWER INTERFACES

    - Provide power interfaces as indicated or as required to control the loads as indicated.

    - General Requirements:

Include the following paragraph to simplify field wiring for the installation contractor and prevent the failure of the interface due to phase to phase overvoltage.

      - Phase independent of control input.

Refer to NFPA 70 (NEC) 300.22, which references UL 2043 in informational note.

      - Rated for use in air-handling spaces as defined in UL 2043.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock. It is common for this leakage current to exceed 5 milliamps (the UL limit for GFCI outlets). Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

      - Utilize air gap off to disconnect the load from line supply.

      - Diagnostics and Service:  Replacing power interface does not require re-programming of system or processor.

    - Product(s):

The following modules take phase control input and provide full circuit of forward/reverse phase control (16 amps) output. The output can be 120V or 277V. This is used for incandescent, magnetic low voltage (MLV), electronic low voltage (ELV), and neon/cold cathode.

      - Phase-Adaptive Power Module; Lutron PHPM-PA:  Provides interface for phase control input to provide full 16 A circuit output of forward/reverse phase control for compatible loads.

The following modules take phase control input and provide full circuit of control (16 amps) output to LED drivers. The output can be 120V or 277V.

      - 3-Wire Fluorescent Power Module; Lutron PHPM-3F:  Provides interface for phase control input to provide full 16 A circuit output for compatible line-voltage control LED drivers.

The following modules take phase control input and provide full circuit switching (16 amps) output. The output can be 120V or 277V. This is used for non-dim loads.

      - Switching Power Module; Lutron PHPM-SW: Provides interface for phase control or switched input to provide full 16 A circuit output of switching for compatible non-dim loads.

The following interfaces take fluorescent ballast control input and provide full circuit of control (16 amps) output to incandescent, electronic low-voltage, magnetic low-voltage, neon, or Advance Mark X lighting sources. Works with 120V control input and 120V or 277V load.

      - Phase-Adaptive Power Module with 3-Wire Fluorescent/LED Input; Lutron PHPM-WBX: Provides interface for fluorescent ballast/LED driver control input to provide full 16 A circuit output for compatible loads.

The following interfaces take phase control input and provide full circuit of switching and 0-10V low voltage output (16 amps) for LED drivers.

      - Ten Volt Interface; Lutron GRX-TVI: Provides interface for phase control input to provide full 16 A circuit output of switching and 0-10 V low voltage control for compatible fluorescent electronic dimming ballasts or LED drivers.

      - Pulse Width Modulation Interface; Lutron GRX-PWM:  Provides interface for phase control input to provide full 16 A circuit output of switching and PWM low voltage control for compatible fluorescent electronic dimming ballasts or LED drivers.

  - LIGHTING CONTROL SYSTEM PROCESSOR

    - Processor; Lutron HomeWorks QSX Processor:

      - Product(s):

        - 1-link processor; Lutron Model HQP7-1.

        - 2-link processor; Lutron Model HQP7-2.

        - 1-link processor for multi-dwelling unit applications; Lutron Model HQP7-MDU-1.

        - 2-link processor for multi-dwelling unit applications; Lutron Model HQP7-MDU-2.

      - Each link configurable for one of the following types:

        - HomeWorks QS Wired Device Link; 99 devices/512 zones.

        - HomeWorks Clear Connect Type A; 99 devices/100 zones.

    - Integrates control station devices, power panels, shades, and external inputs into single customizable, multiple failsafe lighting control system, operable manually or automatically.

    - UL listed.

This statement allows for global control or modification. Without global control, the coordination of multiple databases makes the system difficult to maintain and operate.

    - Multiple processor systems to operate under single database.

Include the following paragraph to allow the system to be integrated with other building management systems.

    - Capable of interfacing to other equipment by means of TCP/IP communication over network.

The integral temperature compensated timeclock ensures that all automatic functions occur at the correct time. Computer timeclocks are inherently unreliable and should not be used. Timeclocks with a large time drift (greater than 2 minutes per year) require regular maintenance.

    - Minimum accuracy of plus/minus 2 minutes per year under all operating conditions.

    - Full internal battery backup capable of storing all system memory for minimum of 1 year without power and automatically returning system to its previous state.

Systems that require a computer to run the timeclock function or run the system database rely on the computer to be operational. If the computer stops working, the entire lighting system stops working. Include the following paragraph to ensure that the lighting system works during a computer failure.

    - Capable of running automatically (timeclock function is retained) and manually (via all wall stations).

    - Processor has LED indicators to display diagnostic information to aid in system set-up and troubleshooting:

      - Confirm proper system communication.

      - Indicate wiring errors between processor and control devices.

    - Software can be upgraded via a local computer or network connection.

    - Processor can communicate to radio frequency lighting control components.

    - Ethernet Capabilities:

      - Provide access to:

        - Scene selections.

        - Fade zone to a level.

        - Ability to flash/warn/chase zone levels.

        - Fine-tuning of preset levels with scene raise/lower.

        - Fine-tuning of light levels with individual zone raise/lower.

        - Enable/disable timeclock.

        - Setting of timeclock.

        - Enable/disable wall station.

        - Simulate wall station button press.

        - Reading/setting of system variables.

        - Provide status monitoring through button feedback and scene-status updates.

      - Ethernet:  Provide ability to communicate by means of TCP/IP over Ethernet to Lighting Control System Processor by means of user-supplied PC or digital audiovisual equipment. Control to be located within 300 feet (100 m) of Ethernet source.

    - Cloud Service Interface:

      - Utilizes TCP/IP communication over Ethernet (internet connection required for initial setup, to maintain system date/time, and receive periodic firmware updates).

      - Allows for system setup, control, and monitoring from iOS or Android mobile device with required Lutron app installed:

        - Allows for adjustment of light and shade levels.

        - Allows for adjustment of system HVAC control temperature settings and schedules.

        - Supports compatible third party Wi-Fi thermostats (requires user-supplied Wi-Fi router); allows for control of temperature setpoints, system mode (e.g. heat, cool, auto, off), and fan on/off status.

        - Allows for timeclock scheduling of events.

        - Allows for mobile device control and monitoring from anywhere in the world.

        - Supports control outside Lutron app via widgets (IOS and Android).

        - Supports Siri and Apple HomeKit technology for up to 150 zones.

      - Provides system remote connectivity capabilities:

        - Supports timeclock synchronization with internet time servers.

  - CENTRALIZED LIGHTING CONTROL SYSTEM SOFTWARE

    - Operates on personal computer (PC) running Windows 10.

    - Allows user in real time (instant changes and feedback to/from the lighting control system) to monitor and control all aspects of lighting control system.

    - Allows user to monitor and control:

      - Current zone intensities.

      - Status of scenes.

      - Enabled/disabled state for the global timeclock.

      - Enabled/disabled state for control station devices.

    - Allows user to create and utilize virtual control station devices.

    - Allows for remote control of physical control station devices.

    - Includes on-screen report capabilities to provide diagnostic information.

    - Provides communication status between all processors and control station devices to verify that connections are sound.

    - Provides for light level intensity values of selected zones over time period.

    - Downloads database to processor(s).

    - Defines, programs, modifies, and updates lighting control system database.

    - Allows user to:

      - Define following within desired space:

        - Zones.

        - Scenes.

        - Timeclock.

        - Control station devices.

        - Switch legs.

      - Define global time clock.

      - Define device functionality as indicated in subsequent sections.

      - Create sequences that can run for specified number of times or until cancelled by user.

      - Lighting levels to fade smoothly between scenes at time intervals of 0 to 4 hours.

      - Define timeclock schedules that can be single or periodic events based on absolute time or time relative to sunrise/sunset.

    - Allows user in real time to recall, redefine, and save zone intensities for selected scene.

    - Real time scene programming software operable on dedicated computer attached to wired or wireless network. User to supply wireless network for wireless operability.

    - Conditional Logic Programming: A desired button action is dependent upon a separate system device, variable state, sequence state, or time.

    - Timeclock:

      - Allows up to 32,000 events to be programmed to occur without user intervention at specified times during the day in relation to sunrise/sunset. Sunrise and sunset times to be calculated by specifying the latitude and longitude of the location of the system.

      - Accurate to plus/minus two minutes per year (specified as during data retention time).

    - Vacation Mode:  Allows user to simulate occupancy for security purposes while away for extended period of time.

    - System integration via IR, CCI, CCO, and/or Ethernet.

    - Mobile Application:

      - Adjust light and shade levels.

      - Control system keypads including button feedback and raise/lower controls.

      - Edit and create time clock events.

      - Edit and create keypad programming for lights, shades, and fans.

      - Adjust temperature settings and schedules.

  - RADIO FREQUENCY (RF) REPEATERS

HomeWorks QS Hybrid Repeaters add wireless Radio Frequency (RF) communication and extend the range of RF signals that are sent between dimmers, switches, keypads, visor control receivers, shades/draperies, and other devices.

    - Product:  Lutron Model HQR-REP-120 HomeWorks Hybrid Repeater.

    - Provide RF repeaters as indicated or as required to facilitate wireless communication between processor and all wireless devices provided.

    - Communications:

      - Wired Communications:  Utilize RS485 wiring for wireless link extension to outbuildings up to 1,000 feet (304 m) between processor and repeater or between repeaters.

      - Wireless Communications:  Communicates directly to compatible RF devices and other RF repeaters through use of a radio frequency communications link; RF range of 30 feet (9 m) between repeater and devices and 60 feet (18 m) between repeaters.

    - Provides wireless communication capability for lighting control system processors via wired communication link.

    - Extends wireless communication range via connection of up to four total repeaters per communications link.

  - CONTROL STATIONS

    - Provide control stations with configuration as indicated or as required to control the loads as indicated.

    - Button-Type Keypads:

      - General Requirements:

        - Allows control of any devices part of the lighting control system.

Controls can be programmed with different functionality through system software without any hardware changes.

        - Allows for easy reprogramming without replacing unit.

        - Buttons/Engraving:

To help facility occupants understand how to use the lighting control system, engraving requirements should be included for all controls. Engraving details should include text size and style.

          - Engrave keypads with button, zone, and scene descriptions <<as indicated on the drawings; to be selected by Architect; or _________>>.

Engraving must be durable when exposed to cleaning and normal wear.

          - Borders, logos, and graduations to use laser engraving or silk-screened graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

Unlike traditional scene control wall stations, centralized low voltage controls can be programmed so that the buttons can have a variety of functions.

        - Software Configuration:

          - Customizable keypad button functionality:

            - Buttons can be programmed to perform single defined action.

            - Buttons can be programmed to perform defined action on press and defined action on release.

            - Buttons can be programmed to perform automatic sequence of defined actions.

            - Capable of deactivating select keypads to prevent accidental changes to light levels.

            - Capable of activating flashing light(s) (panic scene) from a single button press.

        - Status LEDs:

Time delays inherent in large systems can cause short delays between button press and system confirmation. To avoid any confusion and prevent multiple button presses, keypads should immediately show that the button has been pressed for visual confirmation.

          - Upon button press, LEDs to immediately illuminate.

There are two types of keypads; those that only send signals and those that send and receive signals. Having the latter type allows feedback to the user to verify that the request has been received and processed. If the lighting control system fails to process the button press request, the LED will turn off to indicate the true system status.

          - LEDs to reflect the true system status. LEDs to remain illuminated if the button press was properly processed or LEDs to turn off if the button press was not processed.

          - Support logic that defines when LED is illuminated:

            - Scene logic (logic is true when all zones are at defined levels).

            - Room logic (logic is true when at least one zone is on).

            - Pathway (logic is true when at least one zone is on).

      - Wired Keypads; Lutron HomeWorks Wired seeTouch Keypads:

Architectural series keypads use Lutron Nova T* wall plates and are available in insert and non-insert styles. The insert style allows decorator-style controls to be easily ganged. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Style:  <<Architectural Non-Insert Style; Architectural Insert Style; Designer Style>>.

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox or low-voltage mounting bracket; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via the Lutron Designer programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Provide integral infrared receiver for personal control <<where indicated; or _________>>.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Architrave Keypads:

• Available in several button configurations and finishes

• Receives up to two contact closure inputs

• LEDs next to each button are used during programming and provide feedback when the buttons are pressed

• Available with green status and backlight LEDs

      - Wired Keypads; Lutron HomeWorks Wired Architrave Keypads:

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; Lutron Architrave Wallbox; provide wall plates with concealed mounting hardware.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Signature Series Keypads:

• Available in several button configurations and finishes

• Receive up to two contact closure inputs

• LEDs on each button are used during programming and provide feedback when the buttons are pressed

• Large, rounded, backlit buttons with option engraving

• Available with either Green or Blue status and backlight LEDs

      - Wired Keypads; Lutron HomeWorks Wired Signature Series Keypads:

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; Lutron Signature Series Wallbox; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via the Lutron Designer programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

      - Wired Keypads; Lutron HomeWorks Wired Palladiom Keypads:

U.S. style keypads are rectangular, single column. Square style keypads are square, single or double column.

        - Style:  <<U.S. Style; Square Style>>.

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

To provide a clean, minimalist appearance, Palladiom wallstations feature buttons that are flush with the faceplate with minimal gaps and buttons/faceplates with matching material/finishes.

        - Buttons and Faceplate:

          - Buttons to be greater than 0.65 inch (16.5 mm) in height to provide large target area for ease of use and actuation.

          - Front of buttons to be flush with faceplate.

          - Buttons and faceplate to be of the same material (e.g. plastic/plastic, glass/glass, metal/metal).

          - Buttons to depress and provide tactile feedback of a successful button push. Controls utilizing capacitive or resistive touch technology are not acceptable.

          - Gaps to be less than 0.007 inch (0.18 mm) between buttons and less than 0.15 inch (3.8 mm) between buttons and faceplate.

        - Button/Engraving Backlighting:

          - Backlighting to be visible through engraved text to provide clear readability in a variety of lighting conditions.

          - Indicate active scene or room status through the intensity of the backlighting (brighter backlit text indicates the active state).

          - Backlight intensity adjustable via programming software; capable of dynamic adjustment during usage based on conditional logic (time of day, button press, etc.).

        - Design keypads to allow field-customization of button color and engraving using field-changeable replacement kits.

        - Available Palladiom U.S. Style faceplates to accommodate both keypads and Josh.ai Nano home automation microphone.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

      - Wired Keypads; Lutron HomeWorks Wired Alisse Keypads:

        - Style:  Square, international.

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; provide accessory adapter suitable for keypad configuration/number of columns and wallbox shape, e.g. square, round; provide wall plates with concealed mounting hardware.

        - Button Backlighting:

          - Indicate active scene or room status through intensity of backlighting; brighter backlight indicates active state.

          - Backlight intensity adjustable via programming software; capable of dynamic adjustment during usage based on conditional logic, e.g. time of day, button press.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accommodate both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

      - Wireless Keypads; Lutron HomeWorks RF seeTouch Keypads:

Architectural series keypads use Lutron Nova T* wall plates. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Style:  <<Designer Style; Architectural Style>>.

        - Power: 120 VAC, 60 Hz; provide connection as indicated or as required.

        - Communications: Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

Architectural series keypads use Lutron Nova T* wall plates. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via the Lutron Designer programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Available Architectural Style faceplates to accommodate both keypads and Josh.ai Nano home automation microphone.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

      - Wireless Keypads; Lutron HomeWorks Sunnata RF Keypads:

        - Power: 120-277 VAC, 60 Hz; provide connection as indicated or as required.

        - RF Range:  Maximum of 75 feet (22.8 m) between wireless gateway and compatible Clear Connect – Type X wireless devices on same floor; maximum of 25 feet (7.6 m) between each Clear Connect – Type X wireless device and at least two other Clear Connect – Type X wireless devices.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Button Status LEDs:

          - Indicate active scene or room status through intensity of status LEDs; brighter LED indicates active state.

          - Status LED intensity adjustable via programming software; capable of dynamic adjustment during usage based on conditional logic, e.g. time of day, button press.

        - Design keypads to allow field-customization of button color, configuration, and printing using field-changeable replacement kits.

        - Available Architectural Style faceplates to accommodate both keypads and Josh.ai Nano home automation microphone.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

HomeWorks QS RF Hybrid Keypads function as a dimmer and keypad combined into a single device. RF Hybrid Keypads are ideal for retrofit applications since they eliminate the need to install two separate devices.

      - Wireless Keypads with Integral Dimmer; Lutron HomeWorks RF Hybrid seeTouch Keypads:

Architectural series keypads use Lutron Nova T* wall plates. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Style:  <<Designer Style; Architectural Style>>.

        - Integral Dimmer:

          - Suitable for single location and multi-location (with remote dimmer model) installations.

          - Can be assigned to any button on the unit.

          - Can be assigned to any programmable input.

          - Provide manual air gap switch accessible without removing wall plate to facilitate safe lamp replacement.

        - Power: 120 VAC, 60 Hz; provide connection as indicated or as required.

        - Communications: Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

Architectural series keypads use Lutron Nova T* wall plates. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via the Lutron Designer programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Product(s):

        - <<Type _____ - >>Wireless Keypad with Integral Dimmer; Lutron HomeWorks RF C.L Hybrid seeTouch Keypad Series: Dimmable CFL/LED (100 W, 120 V), incandescent/halogen (450 W, 120 V), magnetic low voltage (450 VA/350 W, 120 V), Lutron Hi-Lume 1% 2-wire LED Driver (150 W, 120 V - maximum of 10 drivers); neutral wire required.

HomeWorks Sunnata RF Hybrid Keypads function as a dimmer and keypad combined into a single device. RF Hybrid Keypads are ideal for retrofit applications since they eliminate the need to install two separate devices.

      - Wireless Keypads with Integral Dimmer; Lutron HomeWorks Sunnata RF Hybrid Keypads:

        - Integral Dimmer:

          - Load Type and Capacity:  Dimmable LED/CFL (150 W, 120 V), incandescent/halogen (450 W, 120 V), magnetic low voltage (350 VA/250 W, 120 V), dimmable fluorescent (2.08 A/350 VA, 120 V), Lutron Hi-Lume 1% 2-wire LED Driver (2.08 A/350 VA, 120 V); neutral required.

          - Can be assigned to any button on unit.

          - Can be assigned to any programmable input.

          - Provide manual air gap switch accessible without removing wall plate to facilitate safe lamp replacement.

        - Power: 120 VAC, 60 Hz; provide connection as indicated or as required.

        - RF Range:  Maximum of 75 feet (22.8 m) between wireless gateway and compatible Clear Connect – Type X wireless devices on same floor; maximum of 25 feet (7.6 m) between each Clear Connect – Type X wireless device and at least two other Clear Connect – Type X wireless devices.

Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Button Status LEDs:

          - Indicate active scene or room status through intensity of status LEDs; brighter LED indicates active state.

          - Status LED intensity adjustable via programming software; capable of dynamic adjustment during usage based on conditional logic, e.g. time of day, button press.

        - Design keypads to allow field-customization of button color, configuration, and printing using field-changeable replacement kits.

        - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

The versatile design of HomeWorks QS RF seeTouch Tabletop Keypads allows them to be mounted on a wall, placed on top of a table, or used as a cordless Keypad. The Keypads can be powered by the DC adapter provided with the Keypad or with 2 AAA batteries. Battery powered Tabletop Keypads will shut off after a short period of inactivity in order to conserve battery power.

      - Wireless Tabletop Keypads; Lutron HomeWorks RF seeTouch Tabletop Keypads:

        - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

        - Power: Furnished with provisions for both battery operation and plug-in connection to standard 120 VAC receptacle via supplied DC adapter.

        - Communications: Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

        - Mounting: Suitable for use as a tabletop or handheld remote; provide accessory bracket for optional wall-mounting.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via the Lutron Designer programming software.

        - Design keypads to shut off after a short period of inactivity when operating on battery power.

          - "Wake-Up Only": Single button press to "wake-up" keypad and show status; subsequent press to activate button.

        - Finish: << As indicated on drawings; To be selected by Architect; or __________>>.

The Pico Wireless Control is a flexible and easy to use device that allows the user to control dimmers and switches. The Pico wireless control can function as a tabletop control on a pedestal, a lightweight handheld remote, or it can be wall-mounted with or without a Lutron Claro faceplate, to mimic a traditional keypad. The battery-operated control requires no external power or communication wiring. Models are available with integral night light.

    - Wireless (Radio Frequency) Controls; Lutron Pico Wireless Controls:

      - Product(s):

        - <<Type _____ - >>2-Button Control; Lutron Pico Wireless Control Model PJ2-2B.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>2-Button Control with Night Light; Lutron Pico Wireless Control Model PJN-2B.

        - <<Type _____ - >>2-Button with Raise/Lower Control; Lutron Pico Wireless Control Model PJ2-2BRL.

          - Button Marking:  <<Light (icons); Shade (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button Control; Lutron Pico Wireless Control Model PJ2-3B.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control; Lutron Pico Wireless Control Model PJ2-3BRL.

          - Button Marking:  <<Light (icons); Shade (text); Shade (icons); Blackout (text); Sheer (text); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control and Night Light; Lutron Pico Wireless Control Model PJN-3BRL.

        - <<Type _____ - >>3-Button with Raise/Lower Control for Audio; Lutron Pico Wireless Control Model PJ2-3BRL.

          - Button Marking:  <<Audio (icons and text); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control for Fans; Lutron Pico Wireless Control Model PJ2-3BRL.

          - Button Marking:  <<Fan (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>Paddle Control; Lutron Pico Wireless Control Model PJ2-P2B.

        - <<Type _____ - >>4-Button; Lutron Pico Wireless Control Model PJ2-4B.

          - Button Marking:  <<Zone controls (light); Zone controls (shade); Scene keypads (light); Scene keypads (shade); 2-group controllers (lights); 2-group controllers (shades); 2-group controllers (light and shade); 4-group toggle; As indicated on drawings; Custom engraving to be selected; or __________>>.

        - Single Pedestal; Lutron Pico Pedestal Model L-PED1.

        - Double Pedestal; Lutron Pico Pedestal Model L-PED2.

        - Triple Pedestal; Lutron Pico Pedestal Model L-PED3.

        - Quadruple Pedestal; Lutron Pico Pedestal Model L-PED4.

        - Screw Mounting Kit; Lutron Model PICO-SM-KIT.

        - Wall Plate Adapter; Lutron Model PICO-WBX-ADAPT.

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Communicates via radio frequency to compatible devices.

      - Does not require external power packs, power or communication wiring.

Controls can be programmed with different functionality through system software without any hardware changes.

      - Allows for easy reprogramming without replacing unit.

      - Button Programming:

        - Single action.

      - Includes LED to indicate button press or programming mode status.

      - Wireless Audio Controls:  Allows for control of compatible audio devices (play/pause, skip, cycle between favorite stations, raise/lower volume).

      - Mounting:

        - Capable of being mounted with a table stand or directly to a wall under a faceplate.

        - Faceplates: Provide concealed mounting hardware.

        - Suitable for car visor mounting (with accessory visor clip).

      - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White; Black; Ivory; Light Almond; White/Grey; As indicated on drawings; To be selected by Architect; or __________>>.

Infrared transmitters are used with Lutron-supplied infrared receiver controls. They are used in spaces where remote control is required. Operation is through line-of-sight.

    - Infrared Handheld Controls:

      - Product(s):

        - Four-Scene Wireless Infrared Transmitter; Lutron Model GRX-IT-WH: Operates up to 50 feet (15 m) line-of-sight to receiver.

        - Single-Scene Wireless Infrared Transmitter; Lutron Model C-FLRC-WH: Operates up to 12 feet (3.7 m) line-of-sight to receiver.

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Designed for use in conjunction with compatible infrared receiver and lighting control; compatibility dependent on that receiver, not transmitter.

      - Learnable by other variable frequency remote controls.

HomeWorks QS Visor Controls allow lights, shades/draperies, and other equipment to be controlled from the car with just a touch of a button on a Visor Control Transmitter or a HomeLink compatible visor control.

    - Visor Controls; Lutron HomeWorks Visor Controls:

      - Visor Control Transmitter; Lutron Model LR-3B-H-SW:

        - Designed for use in conjunction with Lutron Visor Control Receiver.

        - Power:  Battery-operated with minimum ten-year battery life.

        - Mounting:  Suitable for car visor mounting with removable visor clip.

        - Finish:  Snow.

        - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Visor Control Receiver; Lutron Model HQR-VCRX-WH:

        - Power:  Plug-in connection to standard 120 VAC receptacle via supplied DC adapter.

        - Communications:  Communicates directly with repeaters and compatible visor control transmitters through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m) between receiver and repeater and 150 feet (46 m) between receiver and transmitter.

        - Contact Closure Interface:

          - Provide two contact closure inputs for integration with other systems; can be configured for maintained or momentary contact closures.

          - Provide one contact closure input for security systems; accepts maintained contact closures.

          - Provide four contact closure outputs for control of garage doors or motorized gates; can be configured for maintained or momentary outputs.

  - WALL DIMMERS, SWITCHES, AND FAN SPEED CONTROLLERS

    - General Requirements:

      - Listed as complying with UL 20 and UL 1472 as applicable.

      - Provides local control in the event that communication with lighting control system is interrupted.

      - Provide air gap service switch accessible without removing wall plate.

HomeWorks QS RF Maestro local controls function much like standard dimmers and switches, but can be controlled as part of a lighting control system. Local lighting controls are useful in locations where single circuits of lighting need to be dimmed or switched.

HomeWorks QS RF Maestro Dimmers incorporate advanced features such as fade on/fade off, delayed long fade to off, and rapid full on.

    - Preset Smart Wall Dimmers and Switches with Wireless Communication; Lutron HomeWorks RF Maestro Series:

Architectural series devices use Lutron Nova T* wall plates. Designer series devices use Lutron Designer (Claro or Satin Colors) wall plates.

      - Style:  <<Designer Style; Architectural Style>>.

      - Communications:  Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

      - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; As indicated on drawings; To be selected by Architect; or __________>>.

      - Dimmer Control: Multi-function tap switch with small, raised rocker for dimmer adjustment.

        - Rocker raises/lowers light level, with new level becoming the current preset level.

        - Switch single tap raises lights to preset level or fades lights to off.

        - Switch double tap raises light to full on level.

        - Switch tap and hold slowly fades lights to off over period of 10 seconds.

        - LEDs adjacent to tap switch indicate light level when dimmer is on, and function as locator light when dimmer is off.

      - Switch Control: Switch single tap turns lights on/off.

      - Dimmer High End Trim:

        - Incandescent Dimmers: Minimum of 92 percent of line voltage.

        - Dimmers for Electronic Low Voltage (ELV) Transformers: Minimum of 95 percent of line voltage.

        - Dimmers for Magnetic Low Voltage Transformers: Minimum of 92 percent of line voltage.

      - Available Architectural Style faceplates to accommodate both dimmers/switches and Josh.ai Nano home automation microphone.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Product(s) - Preset Smart Dimmers with Wireless Communication:

        - <<Type _____ - >>Preset Smart Phase Selectable Dimmer; Lutron HomeWorks RF Maestro Series: Electronic low voltage (500 W, 120 V), dimmable LED (250 W, 120 V), incandescent/halogen (500 W, 120 V), magnetic low voltage (400 VA/300 W, 120 V), Lutron Hi-lume 1% 2-Wire (LTE) LED Driver (400 W, 120 V - maximum of 20 drivers); neutral required or optional depending on load; multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

          - Lutron Model HQRD-PRO (Designer Style); single-pole/multi-location; 120 V.

          - Lutron Model HQRA-PRO (Architectural Style); single-pole/multi-location; 120 V.

        - <<Type _____ - >>Preset Smart Dimmer; Lutron HomeWorks RF Maestro Series: Incandescent (600 W, 120 V), magnetic low voltage (600 VA/450 W, 120 V); neutral required; multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

          - Lutron Model HQRD-6ND (Designer Style); single-pole/multi-location; 120 V.

          - Lutron Model HQRA-6ND (Architectural Style); single-pole/multi-location; 120 V.

        - <<Type _____ - >>Preset Smart Dimmer; Lutron HomeWorks RF Maestro Series: Incandescent (1,000 W, 120 V), magnetic low voltage (1,000 VA/800 W, 120 V); multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

          - Lutron Model HQRD-10D (Designer Style); single-pole/multi-location; 120 V.

          - Lutron Model HQRA-10D (Architectural Style); single-pole/multi-location; 120 V.

        - <<Type _____ - >>Preset Smart Dimmer; Lutron HomeWorks RF Maestro Series: Incandescent (1,000 W, 120 V), magnetic low voltage (1,000 VA/800 W, 120 V); neutral required; multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

          - Lutron Model HQRD-10ND (Designer Style); single-pole/multi-location; 120 V.

          - Lutron Model HQRA-10ND (Architectural Style); single-pole/multi-location; 120 V.

        - <<Type _____ - >>Preset Smart Dimmer; Lutron HomeWorks RF Maestro Series: 3-wire fluorescent ballast/LED driver (6 A, 120-277 V); neutral required; multi-location capability using companion dimmers (up to nine companion dimmers may be connected); minimum load requirement.

          - Lutron Model HQRD-F6AN-DV (Designer Style); single-pole/multi-location; 120-277 V.

          - Lutron Model HQRA-F6AN-DV (Architectural Style); single-pole/multi-location; 120-277 V.

        - <<Type _____ - >>Companion Dimmer: Provides multi-location capability for compatible Lutron HomeWorks RF Maestro Series dimmers.

          - Lutron Model HQD-RD (Designer Style); 120 V.

          - Lutron Model HQA-RD (Architectural Style); 120 V.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Product(s) - Electronic Switches with Wireless Communication:

        - <<Type _____ - >>Electronic Switch; Lutron HomeWorks RF Maestro Series: 8 A lighting/5.8 A fan (120 V); neutral required; multi-location capability using companion switches (up to nine companion switches may be connected); minimum load requirement.

          - Lutron Model HQRD-8ANS (Designer Style); single-pole/multi-location; 120 V.

          - Lutron Model HQRA-8ANS (Architectural Style); single-pole/multi-location; 120 V.

        - <<Type _____ - >>Electronic Switch; Lutron HomeWorks RF Maestro Series: 8 A lighting/3 A fan (120 V); 8 A lighting (277 V); multi-location capability using companion switches (up to nine companion switches may be connected); minimum load requirement.

          - Lutron Model HQRD-8S-DV (Designer Style); single-pole/multi-location; 120-277 V.

          - Lutron Model HQRA-8S-DV (Architectural Style); single-pole/multi-location; 120-277 V.

        - <<Type _____ - >>Companion Switch: Provides multi-location capability for compatible Lutron HomeWorks RF Maestro Series electronic switches.

          - Lutron Model HQD-RS (Designer Style); 120 V.

          - Lutron Model HQA-RS (Architectural Style); 120 V.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Product(s) – Fan Speed Controllers with Wireless Communication:

        - <<Type _____ - >>Fan Speed Controller; Lutron HomeWorks RF Maestro Series: Quiet 4-speed (2 A, 120 V); neutral required; for use with one ceiling paddle fan.

          - Lutron Model HQRD-2ANF (Designer Style); single-pole; 120 V.

          - Lutron Model HQRA-2ANF (Architectural Style); single-pole; 120 V.

    - Paddle Switch/Touch Wall Dimmers, Switches, and Fan Speed Controllers with Wireless Communication; Lutron HomeWorks Sunnata RF Series:

      - RF Range:  Maximum of 71 feet (22 m) between wireless gateway and compatible Clear Connect – Type X wireless devices on same floor; maximum of 25 feet (7.6 m) between each Clear Connect – Type X wireless device and at least two other Clear Connect – Type X wireless devices..

      - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; As indicated on drawings; To be selected by Architect; or __________>>.

      - Switch Control:  Paddle switch for on/off operation.

        - Tap and hold of bottom button for more than one second initiates 30-second delay followed by turning lights off.

        - Advanced Programming Mode: Provides for customized adjustment of functions.

          - LED brightness.

          - Light bar/locator light on/off when lights are on/off.

      - Dimmer Control: Paddle switch with integrated touch LED bar for dimmer adjustment.

        - Single tap of top button fades lights to full on or preset level according to programming.

        - Double tap of top button raises lights to full on.

        - Single tap of bottom button fades lights to off.

        - Tap and hold of bottom button for more than one second initiates 20-second delay followed by 10-second fade of lights to off.

        - LED bar indicates current light level, and functions as locator light when dimmer is off according to programming.

        - Advanced Programming Mode: Provides for customized adjustment of functions.

          - High/low end trims.

          - On to preset level/full on.

          - LED brightness.

          - Light bar/locator light on/off when lights are on/off.

          - Forward/reverse phase dimming.

      - Fan Control: Paddle switch with integrated touch LED bar for fan speed adjustment.

Single tap of top button sets fan to maximum or preset speed according to programming.

        - Double tap of top button sets fan to maximum speed.

        - Single tap of bottom button sets fan to off.

        - LED bar indicates current fan speed, and functions as locator light when fan is off according to programming.

        - Advanced Programming Mode: Provides for customized adjustment of functions.

          - On to maximum/preset speed.

          - LED brightness.

          - Light bar/locator light on/off when fan is on/off.

      - Products – Paddle Switch/Touch Dimmers with Wireless Communication:

        - <<Type _____ - >>Paddle Switch/Touch Dimmer; Lutron HomeWorks Sunnata RF Series: Dimmable LED (250 W, 120 V), incandescent/halogen (500 W, 120 V), magnetic low voltage (400 VA/300 W, 120 V), Lutron Hi-Lume 1% 2-wire LED Driver (400 W, 120 V - maximum of 20 drivers); neutral required; multi-location capability using companion dimmers (up to four companion dimmers may be connected).

          - Lutron Model HRST-PRO-N; single-pole/multi-location; 120 V.

        - <<Type _____ - >>Companion Dimmer:  Provides multi-location capability for compatible Lutron HomeWorks Sunnata RF Series dimmers with true control and LED feedback of light level from all locations.

          - Lutron Model HRST-RD; 120 V.

      - Products – Paddle Switch Electronic Switches with Wireless Communication Inputs:

        - <<Type _____ - >>Paddle Switch/Touch Electronic Switch; Lutron HomeWorks Sunnata RF Series: 8 A lighting, 1/4 HP motor (120 V); neutral required; multi-location capability using companion switches (up to four companion switches may be connected).

          - Lutron Model HRST-8ANS; single-pole/multi-location; 120 V.

        - <<Type _____ - >>Companion Switch:  Provides multi-location capability for compatible Lutron Sunnata RF Series switches with LED feedback of load state from all locations.

          - Lutron Model HRST-RS; 120 V.

      - Products – Paddle Switch/Touch Fan Speed Controllers with Wireless Communication Inputs:

        - <<Type _____ - >>Paddle Switch/Touch Fan Speed Controller; Lutron HomeWorks Sunnata RF Series: Quiet 4-speed (1.5 A, 120 V); neutral required; for use with one ceiling paddle fan.

          - Lutron Model HRST-ANF; single-pole; 120 V.

  - PRESET CONTROLS WITH ZONE OVERRIDE

      - Product(s):

        - Preset controls with wired communications link; Lutron GRAFIK Eye QS.

        - Preset controls with wired or wireless communications link; Lutron GRAFIK EYE QS Wireless.

      - Provide preset controls with configuration and quantity of zones as indicated or as required to control the loads as indicated.

      - Wired Communications:  Utilize RS485 wiring for low-voltage communications link.

      - Wireless Communications:  Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; RF range of 30 feet (9 m).

A surge protector is sold as an accessory to a computer purchase to protect it from lightning strikes or other voltage surges. Likewise, dimmer circuits require surge protection. Surge protection can be built into a dimmer circuit or it can be purchased separately as an external accessory. Include the following paragraph to ensure that the surge protection is built into the dimming system.

      - Surge Tolerance: Designed and tested to withstand surges of 6,000 V, 3,000 amps according to IEEE C62.41.2 and IEC 61000-4-5 without impairment to performance.

      - Finish: <<As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; Standard white with white top door, unless otherwise indicated; Standard white with translucent top door, unless otherwise indicated; Customer colors to be selected by Architect; As indicated on drawings; or __________>>.

To help occupants understand how to use the lighting control system, engraving requirements should be included for all controls. Engraving details should include text size and style.

      - Engrave units with button, zone, and scene descriptions <<As indicated on drawings; To be selected by Architect; or __________>>.

      - Preset Lighting Control with Zone Override:

        - Intensity for each zone indicated by means of one illuminated bar graph per zone.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock. It is common for this leakage current to exceed 5 milliamps (the UL limit for GFCI outlets). Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

        - Utilize air gap off to disconnect the load from line supply.

        - Light intensity with real time energy savings by digital display.

        - Fade time indicated by digital display for current scene while fading.

        - For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

Only include the following paragraph if direct control of motorized shades from unit is required.

      - Preset Window Treatment Control with Zone Override:

        - Preset Expandable Window Treatment Control: Provide up to three columns of window treatment control.

        - For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

  - LOAD CONTROL MODULES

HomeWorks QS RF Plug-In Modules function much like standard lamp dimmers, but can be controlled as part of a lighting control system. RF Plug-In Modules are useful in locations where plug-in table/floor lamps need to be dimmed or non-dimmable plug-in loads need to be switched. RF Plug-In Modules can be hidden discretely behind furniture.

HomeWorks QS RF Plug-In Modules incorporate advanced features such as fade on/fade off, delayed long fade to off, and rapid full on.

    - Wireless Plug-In Modules; Lutron HomeWorks RF Series:

      - Communications:  Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

      - Power:  Plug-in connection to standard 120 VAC receptacle.

      - Finish: <<As indicated on drawings; To be selected by Architect; or __________>>.

      - Tabletop Lamp Dimmer:

        - Product:  Single receptacle lamp dimmer with local dimming control; Lutron Model HQR-3LD; load rating of 300 W for incandescent/halogen and 200 W/300 VA for magnetic low voltage.

        - Provides dimming control of connected table/floor lamps.

        - Furnished with local dimming control, connected by cord 6 feet (1.8 m) in length.

        - Standby Power Draw:  Less than 0.5 W.

        - Dimmer:  High end to be a minimum of 92 percent of line voltage.

        - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Plug-In Dimming Module:

        - Product:  Single receptacle plug-in dimmer; Lutron Model HQR-3PD-1; load rating of 300 W for incandescent/halogen and 200W/300 VA for magnetic low voltage.

        - Provides dimming/switching control of plug-in incandescent lamp loads.

        - Standby Power Draw:  Less than 0.5 W.

        - Dimmer:  High end to be a minimum of 92 percent of line voltage.

        - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Plug-In Switching Module:

        - Product:  Three receptacle plug-in switch; Lutron Model HQR-15APS-1; load rating of 1/2HP or 15 A for general purpose.

        - Provides switching control of plug-in general purpose loads.

        - Standby Power Draw:  Less than 0.5 W.

        - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

    - Outdoor Plug-In Switch:

      - Product:  Single receptacle outdoor plug-in switch; Lutron Model HQR-15OUT-BL; load rating of 1/2HP for motor/pump loads, 15 A for lighting loads, and 1,200 VA for lighting transformer/magnetic ballast loads.

      - Provides switching control of plug-in outdoor lighting, motors/pumps, and lighting low-voltage transformers.

      - Communications:  Communicates directly to compatible Clear Connect – Type A RF receiving devices through use of radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

      - Power:  Plug-in connection to standard 120 VAC receptacle.

      - IEC 60529, IP 66 rating.

      - Finish:  Black.

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

    - Wireless Junction Box-Mounted Modules:

      - Communications:  Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

      - Plenum rated.

      - Dimming Module:

        - Product:  Lutron RF Dimming Module Model LMJ-5T-DV-B.

IEC 60929 is a standard for electronic fluorescent ballasts, and is used by other lighting equipment controlled by low voltage signals including LED drivers and low voltage controlled neon. It defines specific methods for 0-10V, pulse width modulation (PWM), and Digitally Addressable Lighting Interface (DALI).

        - Single low voltage dimming module with Class 1 or Class 2 isolated 0-10V output signal conforming to IEC 60929 Annex E.2; source or sink automatically configures.

        - 60 mA of 0-10 V dimming (approximately 30 drivers).

        - Configurable high- and low-end trim.

        - Relay: 5 A; rated for 0-10 V LED drivers or fixtures that conform with NEMA 410.

      - Relay Module:

        - Product:  Lutron RF Relay Module Model LMJ-16R-DV-B.

Lutron Softswitch circuitry prevents arcing at the relay contacts for all three load types, and extends the relay life in excess of one million cycles. Switching high inrush loads can damage relay controls over time. The arcing of these relays, depending on load, typically will limit relay life to 10,000 or 50,000 cycles.

        - Rated Life of Relay: Typical of 1,000,000 cycles at fully rated 16 A for all lighting loads.

        - Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

        - Fully rated output continuous duty for inductive, capacitive, and resistive loads.

      - Contact Closure Output Module:

        - Product: Lutron RF Single CCO Module Model LMJ-CCO1-24-B

        - Single contact closure output including both normally open and normally closed dry contacts.

        - Maintained or momentary output.

        - Powered via 24VDC or 24VAC (transformer not included).

    - DIN Rail Power Modules:

      - Power Module General Requirements:

        - Surge Tolerance: Designed and tested to withstand surges of 6,000 V, 3,000 amps according to IEEE C62.41.2 and IEC 61000-4-5 without impairment to performance.

        - Power:  120 VAC, 50/60 Hz; provide connection as indicated or as required.

        - Communications:  Utilize RS485 wiring for low-voltage communications link.

        - Passively cooled via free-convection, unaided by fans or other means.

        - Provide LED indicators for displaying diagnostic information.

      - Switching Power Modules:

        - Product(s):  Lutron Switching Power Module; Model LQSE-4S8-120-D; 4-zone.

        - Output Zones:  Each zone rated at 8 A for resistive, inductive, or capacitive lighting loads as defined by IEC 60669-2-1 and NEMA 410, or 1/3 HP motor load; maximum of 16 A per module.

        - Manual Mode Operation:  Provide buttons to turn loads on/off for each zone.

        - Manual Override Contact Closure Input:  Provides activation of manual override mode; turns all loads on and disables control from other devices.

        - Contact Closure Output:

          - Single contact closure output including both normally open and normally closed dry contacts.

          - Maintained or momentary output.

          - Inductive Loads:  Provide flyback diode wired per manufacturer’s instructions to control unclamped inductive loads such as relays, solenoids, and motors.

      - Phase Adaptive Power Modules:

        - Product(s):

          - Lutron Adaptive Power Module; Model LQSE-4A5-120-D; 4-zone.

            - Zone 1:  Rated for incandescent/halogen (800 W, 120 V), electronic low voltage (800 W, 120 V), magnetic low voltage (800 VA/525 W, 120 V), or neon/cold cathode (800 VA/525 W, 120 V), Lutron Hi-lume 1% 2-wire LED Driver (maximum of 20 drivers), NEMA SSL 7A forward phase LED (400 W, 120 V).

            - Zones 2 through 4:  Each zone rated for incandescent/halogen (500 W, 120 V), electronic low voltage (500 W, 120 V), magnetic low voltage (500 VA/375 W, 120 V), or neon/cold cathode (500 VA/375 W, 120 V), Lutron Hi-lume 1% 2-wire LED Driver (maximum of 13 drivers), NEMA SSL 7A forward phase LED (200 W, 120 V).

        - Provides leading-edge or trailing-edge dimming; automatic or manual configuration.

        - Output Zones:  One load type per zone.

        - Manual Mode Operation:  Provide buttons to turn loads on/off or dim loads up/down for each zone.

        - Manual Override Contact Closure Input:  Provides activation of manual override mode; turns all loads on and disables control from other devices.

        - Provide cycle-by-cycle compensation for incoming line voltage variations, including changes in voltage, frequency shifts, harmonics, and line noise; accommodate up to plus/minus two percent change in frequency per second.

        - Systems not providing cycle-by-cycle compensation to include external power conditioning equipment as part of dimming system.

        - Comply with NEMA SSL 7A.

      - 0-10 V Power Modules:

        - Products:

          - Lutron 0-10 V Power Module; Model LQSE-4T5-120-D; 4-zone.

            - Each zone rated at 5 A, 120 V for switching of incandescent, electronic low voltage, magnetic low voltage, and LED lighting loads.

            - Each zone provides 50 mA of 0-10 V dimming control conforming to IEC 60929 Annex E.2; source or sink automatically configures.

          - Lutron 0-10 V/Softswitch Power Module, Model LQSE-4T20-120-D; 4-zone.

            - Each zone rated for switching of tungsten (20 A, 120 V), AC general use (20 A, 120 V), electric discharge lamp (16 A, 120 V), LED drivers and fluorescent ballasts (16 A, 120 V), resistive (20 A, 120 V), inductive (20 A, 120 V), motor (1.0 HP, 120 V).

            - Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

            - Rated Life of Relay:  Typical of 1,000,000 cycles at rated load.

            - Each zone provides 50 mA of 0-10 V dimming control conforming to IEC 60929 Annex E.2; source or sink automatically configures; ANSI C173.1 standby/electronic off mode.

        - Manual Mode Operation:  Provide buttons to turn loads on/off or dim loads up/down for each zone.

        - Manual Override Contact Closure Input:  Provides activation of manual override mode; turns all loads on and disables control from other devices.

      - Digital Fixture Control Modules:

        - Product:  Lutron Power Module with HomeWorks Digital; Model LQSE-2HDC-D; two HomeWorks Digital Links.

        - Provide testing capability using manual override buttons.

        - Each low-voltage digital communication link to support up to 64 LED drivers capable of NFPA 70 Class 1 or Class 2 installation.

      - DALI Fixture Control Modules:

        - DALI-2 certified.

        - Products:

          - Lutron DALI Power Module; Model LQSE-1DAL2-D; 120/220-240 VAC; provides up to 250 mA bus power and control for one DALI bus supporting up to 64 DALI-compliant addressable loads and 64 zones.

            - Manual Override Contact Closure Input:  Provides activation of manual override mode; turns all loads on and disables control from other devices.

      - Motor Control Power Modules:

        - Product:  Lutron Motor Control Power Module; Model LQSE-4M-120-D; 4-zone.

        - Output Zones:  Each zone rated at 5 A (1/4 HP) for motor loads (not rated for non-motor loads); maximum of 16 A per module; one motor per zone.

        - Manual Mode Operation:  Provide buttons to raise/lower loads for each zone.

        - Provide configurable minimum on time (jog time), interlock delay, and maximum on time.

      - DIN Rail Feed-Through Panels:  Provide as indicated or as required to house system components.

        - Rated for feed-through, 120 VAC applications.

        - Surface or flush mounting.

        - Product(s):

          - Lutron Model PD2-16T-DV Satellite Panel; 16 inches (40.7 cm) high, nominal; for housing up to two DIN rail power modules and one wire landing board.

          - Lutron Model PD4-42T-DV Control Panel; 42 inches (107 cm) high, nominal; for housing up to four DIN rail power modules, four wire landing boards, two power supplies, and two low-voltage interfaces or processors.

          - Lutron Model PD6-42T-DV Satellite Panel; 42 inches (107 cm) high, nominal; for housing up to six DIN rail power modules and one wire landing board.

          - Lutron Model PD8-65T-DV Control Panel; 65 inches (165 cm) high, nominal; for housing up to eight DIN rail power modules, four wire landing boards, two power supplies, and two low-voltage interfaces or processors.

          - Lutron Model PD10-65T-DV Satellite Panel; 65 inches (165 cm) high, nominal; for housing up to ten DIN rail power modules and one wire landing board.

      - DIN Rail Breaker Panels:  Provide with configurations as indicated or as required.

        - Passively cooled via free-convection, unaided by fans or other means.

        - Shipped with each dimmer position in mechanical bypass by means of jumper bar inserted between input and load terminals. Jumpers to carry full rated load current and be reusable at any time. Mechanical bypass device to allow for switching operation of connected load with dimmer removed by means of circuit breaker.

        - Furnished with eight factory-installed combination type arc fault circuit breakers.

          - Listed to UL 489 as molded case circuit breaker for use on lighting circuits.

          - Provided with visual trip indicator.

          - Provide circuit breakers with interrupting capacity as required to provide the short circuit current rating <<indicated, but not less than:; indicated.; or __________>>

            - <<10,000; or __________>> rms symmetrical amperes at 120 VAC.

        - Provide capacity for field-installation of four additional Square D QO Series plug-in general branch circuit breakers.

        - Provide capacity for up to eight DIN rail power modules and one wire landing board.

        - Surface or flush mounting.

        - Product(s):

          - 120/240 VAC main lug only panel with 15A AFCI branch breakers; Lutron Model PD8-65A-120L3-15.

          - 120/240  VAC main lug only panel with 20A AFCI branch breakers; Lutron Model PD8-65A-120L3-20.

          - 120/208 VAC main lug only panel with 15A AFCI branch breakers; Lutron Model PD8-65A-120L4-15.

          - 120/208  VAC main lug only panel with 20A AFCI branch breakers; Lutron Model PD8-65A-120L4-20.

      - DIN Retrofit Subplates:  Provide as indicated or as required to mount DIN rail power modules in existing compatible panels/enclosures.

        - Provide capacity for up to eight DIN rail power modules and one wire landing board.

        - Includes one QS link wiring harness and one QS wire landing board.

        - Rated for 120 VAC applications.

        - Designed to permit existing terminal blocks and field wiring to remain intact.

        - Products:

          - DIN rail retrofit subplate for Lutron remote power panels; Lutron Model PD8-PNL-8-SUB.

          - DIN rail retrofit subplate for LiteTouch enclosures; Lutron Model HWR-PD-8-120FT.

These interfaces enable the lighting control system to receive or send a control signal to or from another system (Occupancy, A/V, shades). Include this article if control over the system through external inputs such as contact closure, Ethernet, RS232, etc. is required.

  - LOW-VOLTAGE CONTROL INTERFACES

    - Provide low-voltage control interfaces as indicated or as required to control the loads as indicated.

    - Connects to system using wired communication link.

    - Contact Closure Interface:

      - Product:  Lutron Model QSE-IO.

      - The contact closure input device to accept both momentary and maintained contact closures.

      - The contact closure output device can be configured for maintained or pulsed outputs.

    - Wallbox Input Closure Interface:

      - Product: Lutron Model QSE-CI-WCI.

      - Mounts in wallbox behind contact closure keypad to provide interface for up to eight contact closure inputs.

      - The contact closure input device to accept both momentary and maintained contact closures.

    - DMX Interface:

      - Product:  Lutron Model QSE-CI-DMX.

      - Provides control of 32 DMX channels.

      - Supports single and three channel loads.

      - HWQS programming software used to set color table and associated channels for both RGB and CMY.

The QS Sensor Module (QSM) is a ceiling-mounted device that integrates Lutron wireless and wired sensors and controls through the QS communication link.

    - Sensor Modules:

      - Products:

Capabilities of the following module:

Up to 4 wired sensors per module

Maximum of 10 wireless occupancy sensors

Maximum of 10 wireless controllers

Sensor Module wireless range:

60 ft (18 m) line of sight

30 ft (9 m) through walls

        - Sensor module with both wired and wireless inputs; Lutron Model QSM2-4W-C.

Capabilities of the following module:

Up to 4 wired sensors per module

        - Sensor module with wired inputs only; Lutron Model QSMX-4W-C.

Capabilities of the following module:

Maximum of 10 wireless occupancy sensors

Maximum of 10 wireless controllers

Sensor Module wireless range:

60 ft (18 m) line of sight

30 ft (9 m) through walls

        - Sensor module with wireless inputs only; Lutron Model QSM2-XW-C.

      - Wired Modules:

        - Provide wired inputs for:

          - Up to four occupancy sensors.

      - Wireless Modules:

        - Provide wireless communication inputs for:

          - Up to 10 occupancy/vacancy sensors.

          - Up to 10 wireless controllers.

          - Up to 5 radio window sensor pairs.

        - RF Range: 30 feet (9 m) between sensor and compatible RF receiving devices.

        - RF Frequency: 434 MHz; operates in FCC governed frequency spectrum for periodic operation; continuous transmission spectrum is not permitted.

      - Communicate sensor information to wired low-voltage digital link for use by compatible devices.

    - Wireless Processor:

      - Product:  Lutron HomeWorks Wireless Processor; Model HQP7-RF-2.

      - Connects to lighting management hub via system Ethernet link through PoE switch.

      - Enables lighting control system to communicate with up to 100 Clear Connect – Type X wireless devices, including Ketra intelligent light sources, 95 Clear Connect – Type A wireless devices, and 4 Type A repeaters per gateway.

      - RF Range:

        - Maximum of 75 feet (23 m) between wireless gateway and compatible Clear Connect – Type X wireless devices on same floor; maximum of 25 feet (7.6 m) between each Clear Connect – Type X wireless device and at least two other Clear Connect – Type X wireless devices.

        - Maximum of 30 feet (9 m) between wireless gateway or Type A repeater and Clear Connect – Type A devices and 60 feet (18 m) between Type A repeaters.

    - Wireless Gateway:

      - Product:  Lutron HomeWorks Clear Connect Gateway – Type X; Model HQP7-RF.

      - Connects to lighting management hub via system Ethernet link through PoE switch.

      - Enables lighting control system to communicate with up to 100 Clear Connect – Type X wireless devices, including Ketra intelligent light sources.

      - RF Range:  Maximum of 75 feet (23 m) between wireless gateway and compatible Clear Connect – Type X wireless devices on same floor; maximum of 25 feet (7.6 m) between each Clear Connect – Type X wireless device and at least two other Clear Connect – Type X wireless devices.

  - HVAC CONTROLS

    - HVAC Controls:  Provided by Lighting Control Manufacturer, for system control interface.

    - Wireless Controls:

      - System Capabilities:

        - Utilizes cloud communication with lighting control system and wired connection with HVAC equipment.

        - 7-day programmable schedule.

        - Interfaces Lutron mobile device applications.

      - Product(s):

Thermostat can only be used in systems that are programmed using the PC programming tool.

        - Wireless Thermostat; Lutron Model L-HWLV2-WIFI Lutron Wireless Thermostat.

          - Utilizes existing Wi-Fi network.

          - Controls humidification, dehumidification, and ventilation.

          - Universal input for wired indoor, outdoor, or discharge sensor.

    - Wired Controls; Lutron HomeWorks Palladiom HVAC Solution:

      - System Capabilities:

        - 7-day programmable schedule.

        - Provides local control in the event that communication with lighting control system is interrupted.

        - Interfaces with Lutron mobile device application.

        - Supports control of compatible residential HVAC systems with required HVAC controllers and/or system interfaces, including but not limited to:

          - Conventional forced air systems using gas, electric, or oil heat, as well as compressor-based cooling-only as split systems or packaged units.

          - Heat pumps with or without auxiliary heat.

          - Fan coil units.

          - Hydronic or electric underfloor/radiant heating; capable of controlling room air temperature, floor temperature, or room air temperature with floor temperature limits.

          - VRV/VRF systems.

      - Room Thermostat:

        - Product:  Lutron HomeWorks Palladiom Thermostat.

        - Power:  Class 2 (low voltage).

        - Communications:

          - Utilize RS485 wiring for low-voltage communications link with lighting control system.

          - Utilize Modbus wiring for low-voltage communications link with HVAC control system.

        - Master/Companion Thermostat Capability:

          - Supports connection of up to four Palladiom room thermostats per zone (one master thermostat and up to three companion thermostats).

          - Master Thermostat:  Reports temperature to companion thermostats; connects directly to HVAC controller or system interface.

          - Companion Thermostat:  Permits user adjustment of master thermostat temperature setpoint.

        - Mounting:  Wallbox; Lutron Model EBB-1-SQ.

        - Button/Display Backlighting:

          - Turns on when any button is pressed and turns off after 10 seconds of inactivity.

          - Backlight intensity adjustable via programming software; capable of dynamic adjustment during usage based on conditional logic (time of day, button press, etc.).

        - Temperature Setpoint/Display:

          - Temperature Setpoint:  Adjustable in 1 degree F (0.5 degree C) increments.

          - Temperature Display:  Displays in 1 degree F (0.5 degree C) increments.

          - Can be toggled between Fahrenheit and Celsius units.

          - Display Range:  32 to 99 degrees F (0 to 37 degrees C).

        - Room Temperature Sensor:

          - Accuracy:  Plus/minus 1 degree F at 70 degrees F (0.5 degrees C at 25 degrees C).

          - Temperature Calibration Range:  Plus/minus 5 degrees F (3 degrees C).

Palladiom devices feature matching buttons and faceplates (e.g. plastic/plastic, glass/glass, metal/metal).

        - Provide matching material/finish for buttons and wall plates.

        - Finish: << As specified for wall controls in "Device Finishes" under LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

      - Provide HVAC controllers as required to control HVAC system.

        - Product:  Lutron Model SMC55-RESI-2 Palladiom HVAC Controller (includes required Lutron Model LR-HVAC-WIRE-120 wire harness).

        - Supports connection of wired remote temperature sensor; when used, provides continued operation in the event that communication with room thermostat is interrupted.

        - Supports connection of wired floor temperature sensor for radiant underfloor heating.

      - Provide remote temperature sensors <<where indicated; or __________>>.

        - Product:  Lutron Model LR-TEMP-FLSH wired flush mount sensor.

  - WIRED SENSORS

    - Wired Occupancy Sensors:

      - General Requirements:

        - Connects directly to compatible modules without the need of a power pack or other interface.

        - Turns off or reduces lighting automatically after reasonable time delay when a room or area is vacated by the last person to occupy the space.

        - Accommodates all conditions of space utilization and all irregular work hours and habits.

        - Comply with UL 94.

The self-adaptive internal microprocessor analyzes the signals to eliminate time-consuming adjustments and callbacks found in non-intelligent sensors.

        - Self-Adaptive:  Continually adjusts sensitivity and timing to ensure optimal lighting control for any use of the space.

        - Furnished with field-adjustable controls for time delay and sensitivity to override any adaptive features.

        - Provide capability to:

          - Add additional timeout system-wide without need to make local adjustment on sensor.

          - Group multiple sensors.

Power dropouts occur frequently. When power is restored, the lighting system should recover quickly and automatically return to the last lighting levels. A momentary interruption (1 or 2 seconds) of power should not cause extended periods (20 seconds or more) without lighting while the system reboots and all other electrical equipment is back on.

        - Power Failure Memory:  Settings and learned parameters to be saved in non-volatile memory and not lost should power be interrupted and subsequently restored.

        - Furnished with all necessary mounting hardware and instructions.

        - Class 2 devices.

        - Ceiling-Mounted Sensors:  Indicate viewing directions on mounting bracket.

        - Wall-Mounted Sensors:  Provide swivel-mount base.

        - Color:  White.

Ceiling- and wall-mounted sensors using passive infrared (PIR) technology sense occupancy by detecting the difference between heat emitted from the human body in motion and background space. PIR sensors are good at detecting major motion and require an unobstructed line-of-sight for accurate detection. Ceiling-mounted sensors are recommended for larger open spaces with ceilings less than 12 feet high. Wall-mounted sensors are recommended for spaces with pendant fixtures, ceiling fans, or ceilings more than 12 feet high.

      - Wired Passive Infrared Sensors:

Include the following paragraph to ensure that the line-of-sight is not obstructed due to dust and other contaminants.

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

        - Ceiling-Mounted Sensors:  Provide customizable mask to block off unwanted viewing areas.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

          - <<Type _____ - >>Ceiling-Mounted Passive Infrared Sensor, 450 square feet (42 sq m); Lutron Model LOS-CIR-450-WH: Coverage of 450 square feet (42 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Passive Infrared Sensor, 1500 square feet (140 sq m); Lutron Model LOS-CIR-1500-WH: Coverage of 1500 square feet (140 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

          - <<Type _____ - >>Wall-Mounted Passive Infrared Sensor; Lutron Model LOS-WIR-WH:  Coverage of 1600 square feet (149 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 110 degree field of view.

Ceiling-mounted sensors using ultrasonic technology sense occupancy by bouncing ultrasonic sound waves (32kHz-45kHz) off objects in a space and detecting a frequency shift between emitted and reflected sound waves. Ultrasonic sensors are good at detecting minor motion and do not require an unobstructed line-of-sight. Ceiling-mounted sensors are recommended for larger open spaces with ceilings less than 12 feet high.

      - Wired Ultrasonic Sensors:

The intent of the following paragraph is to eliminate sensor cross talk and assure reliable performance.

        - Utilize an operating frequency of 32kHz or 40kHz, crystal-controlled to operate within plus/minus 0.005 percent tolerance.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

          - <<Type _____ - >>Ceiling-Mounted Ultrasonic Sensor, 500 square feet (46 sq m); Lutron Model LOS-CUS-500-WH: Coverage of 500 square feet (46 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Ultrasonic Sensor, 1000 square feet (93 sq m); Lutron Model LOS-CUS-1000-WH: Coverage of 1,000 square feet (93 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Ultrasonic Sensor, 2000 square feet (186 sq m); Lutron Model LOS-CUS-2000-WH: Coverage of 2000 square feet (186 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

Ceiling-and wall-mounted dual technology sensors use both passive infrared and ultrasonic technologies for sensing occupancy providing maximum reliability. Ceiling-mounted sensors are recommended for larger open spaces with ceilings less than 12 feet height. Wall-mounted sensors are recommended for spaces with pendant fixtures, ceiling fans, or ceilings more than 12 feet high.

      - Wired Dual Technology Sensors:

Include the following paragraph to ensure that the line-of-sight is not obstructed due to dust and other contaminants.

        - Passive Infrared:  Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Include the following paragraph to eliminate sensor cross talk and assure reliable performance.

        - Ultrasonic:  Utilize an operating frequency of 32kHz or 40kHz, crystal-controlled to operate within plus/minus 0.005 percent tolerance.

        - Ceiling-Mounted Sensors:  Provide customizable mask to block off unwanted viewing areas.

Omit the optional choice in the following paragraph if only models with isolated relay will be used.

Contact Rating (R Models only)

SPDT 500mA rated at 24V isolated relay.

        - Isolated Relay:  Provide an internal additional isolated relay with Normally Open, Normally Closed, and Common outputs for use with HVAC control, Data Logging and other control options<< where indicated>>.

Omit the optional choice in the following paragraph if only models with integral photocell will be used.

PhotoCell (R Models only)

-Prevents light from turning on when there is sufficient natural light

-Sensitivity: 0-1,000 LUX adjustable

        - Integral Photocell:  Provide an integral photocell with adjustable sensitivity to prevent lights from turning on when there is sufficient natural light<< where indicated>>.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s), Without Isolated Relay and Integral Photocell:

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 500 square feet (46 sq m); Lutron Model LOS-CDT-500-WH: Coverage of 500 square feet (46 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 1000 square feet (93 sq m); Lutron Model LOS-CDT-1000-WH: Coverage of 1000 square feet (93 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 2000 square feet (186 sq m); Lutron Model LOS-CDT-2000-WH: Coverage of 2000 square feet (186 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

          - <<Type _____ - >>Wall-Mounted Dual Technology Sensor; Lutron Model LOS-WDT-WH: Coverage of 1600 square feet (149 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 110 degree field of view.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s), With Isolated Relay and Integral Photocell:

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 500 square feet (46 sq m); Lutron Model LOS-CDT-500R-WH: Coverage of 500 square feet (46 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 180 degree field of view; with isolated relay and integral photocell.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 1000 square feet (93 sq m); Lutron Model LOS-CDT-1000R-WH: Coverage of 1000 square feet (93 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 180 degree field of view; with isolated relay and integral photocell.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 2000 square feet (186 sq m); Lutron Model LOS-CDT-2000R-WH: Coverage of 2000 square feet (186 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view; with isolated relay and integral photocell.

          - <<Type _____ - >>Wall-Mounted Dual Technology Sensor; Lutron Model LOS-WDT-R-WH:  Coverage of 1600 square feet (149 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 110 degree field of view; with isolated relay and integral photocell.

    - Sensor Power Packs:

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Product(s):

        - <<Type _____ - >>347 VAC power input/24 VDC, 100 mA power output; 15 A ballast (347 V) relay contact rating; Lutron Model PP-347H Power Pack.

        - <<Type _____ - >>120-277 VAC power input/24 VDC, 150 mA power output; 16 A lighting (120-177 V), 1 HP motor (120-277 V) relay contact rating; Lutron Model PP-DV Power Pack.

        - <<Type _____ - >>120-277 VAC power input (manual)/24 VDC, 150 mA power output; 16 A lighting (120-177 V), 1 HP motor (120-277 V) relay contact rating; Lutron Model PP-DV-M Power Pack.

        - <<Type _____ - >>Control relay only (no power input/output); requires another power pack for power and counts as one of three sensors connected to a power pack; 16 A lighting (120-277 V), 1 HP motor (120-277 V), 15 A ballast (347 V) relay contact rating; Lutron Model PP-SH Power Pack.

      - Provide sensor power packs where required for power connection to sensors.

      - For ease of mounting, installation and future service, power pack(s) to be able to mount through a 1/2 inch knockout in a standard electrical enclosure and be an integrated, self-contained unit consisting internally of an isolated load switching control relay and a transformer to provide low-voltage power. Transformer to provide power to a minimum of three sensors.

      - Plenum-rated.

      - Control Wiring Between Sensors and Control Units:  Class 2, 18-24 AWG, stranded UL Classified, PVC insulated or TEFLON jacketed cable suitable for use in plenums, where applicable.

The CES daylight sensor package allows Lutron lighting control systems to respond to ambient light levels based on the settings of the controller. The package includes a power pack, CES daylight sensor, and LC8 controller. It can be integrated via contact closure into a variety of Lutron lighting systems.

-Allows management of Lutron lighting control systems through dry contact closure outputs from the LC8 controller

-The controller features adjustable On and Off setpoints

-The package can be integrated into any Lutron system that accepts dry contact closure inputs

-A variety of sensor types are available to fit any application

    - Daylight Control Package:

      - Product:  Lutron CES Series (Lutron CES Analog Sensor, LC8 Controller, and Power Pack).

      - Controller:

        - Product:  Lutron Model LC8.

        - Automatically switches a dry contact according to changes in ambient light levels.

        - Fully adjustable separate high and low setpoints, with an adjustable dead band between set points to prevent unwanted cycling.

        - Input time delay to prevent unwanted cycling due to intermittent light level fluctuations.

        - Signal/setpoint and relay status indication.

        - Lutron CES sensor calibration input.

      - Sensors:

        - Class 2, three-wire analog devices.

        - Provision for zero or offset based signal.

        - Indoor Photo Sensors; Lutron Model CES/I:  With fresnel lens and 60 degree cone of response; sensor range of 0 to 750 footcandles.

        - Outdoor Photo Sensors; Lutron Model CES/O:  Weatherproof, with hood over aperture to shield sensor from direct sunlight; sensor range of 0 to 750 footcandles.

        - Atrium Photo Sensors; Lutron Model CES/A:  With translucent dome and 180 degree field of view; sensor range of 2 to 2,500 footcandles.

        - Skylight Photo Sensors; Lutron Model CES/S:  With translucent dome and 180 degree field of view; sensor range of 10 to 7,500 footcandles.

Include the following paragraph for automatic detection of partition status. Sensor will supply signal to the centralized lighting control system to automatically reconfigure the space depending on the status of the partition.

    - Infrared Partition Sensors:

      - Product:  Lutron Model GRX-IRPS-WH.

      - Provide contact closure based on status of the partition wall (open/close) enabling automatic linking of controls.

  - WIRELESS SENSORS

    - General Requirements:

      - Operational life of 10 years without the need to replace batteries when installed per manufacturer's instructions.

      - Communicates directly to compatible RF receiving devices through use of a radio frequency communications link.

      - Does not require external power packs, power wiring, or communication wiring.

      - Capable of being placed in test mode to verify correct operation from the face of the unit.

      - RF Range to RF Repeater:  30 feet (9 m) through typical construction materials.

The FCC sets limits on EMI/RFI for both non-consumer (commercial and industrial) and consumer (residential) applications. The class B, consumer limits are more stringent than the class A, non-consumer limits.

      - Electromagnetic Interference/Radio Frequency Interference (EMI/RFI) Limits:  Comply with FCC requirements of CFR, Title 47, Part 15, for Class B application.

Lutron's occupancy/vacancy sensors are wireless, battery-powered passive infrared (PIR) sensors that automatically control lights via RF communication to compatible dimming and switching devices. These sensors detect the heat from people moving within an area to determine when the space is occupied. The sensors then wirelessly transmit the appropriate commands to the associated dimming and switching devices to turn the lights on or off automatically. They combine both convenience and exceptional energy savings along with ease of installation.

    - Wireless Occupancy/Vacancy Sensors:

      - General Requirements:

        - Provides a clearly visible method of indication to verify that motion is being detected during testing and that the unit is communicating to compatible RF receiving devices.

Include the following paragraph to ensure that the line-of-sight is not obstructed due to dust and other contaminants.

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Lutron's XCT signal processing technology greatly enhances the performance of PIR sensors, enabling them to "see" fine motions that other sensors couldn't previously detect. Plus, the user-replaceable batteries are designed to last up to 10 years.

        - Sensing Mechanism:  Passive infrared coupled with technology for sensing fine motions; Lutron XCT Technology. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor's sensitivity threshold.

        - Provide optional, readily accessible, user-adjustable controls for timeout, automatic/manual-on, and sensitivity.

        - Turns off lighting after reasonable and adjustable time delay once the last person to occupy the space vacates a room or area. Provide adjustable timeout settings of 1, 5, 15, and 30 minutes.

          - Additional sensor timeout of up to 300 minutes is available through Lutron Designer programming software.

        - Can be programmed to control anything in the HomeWorks system using the programming software.

        - Color:  White.

        - Provide all necessary mounting hardware and instructions for both temporary and permanent mounting.

        - Provide temporary mounting means to allow user to check proper performance and relocate as needed before permanently mounting sensor. Temporary mounting method to be design for easy, damage-free removal.

        - Sensor lens to illuminate during test mode when motion is detected to allow installer to verify coverage prior to permanent mounting.

        - Ceiling-Mounted Sensors:

          - Provide surface mounting bracket compatible with drywall, plaster, wood, concrete, and compressed fiber ceilings.

          - Provide recessed mounting bracket compatible with drywall and compressed fiber ceilings.

          - Provide customizable mask to block off unwanted viewing areas.

        - Wall-Mounted Sensors:  Provide wall or corner mounting brackets compatible with drywall and plaster walls.

      - Wireless Combination Occupancy/Vacancy Sensors:

-Wireless occupancy sensor has three settings available: Auto-On/Auto-Off, Auto-On Low-Light/Auto-Off, and Manual-On/Auto-Off

-Auto-On Low-Light feature will only turn lights on automatically if there is less than approximately 1 fc (10 lux) of ambient light

-Simple and intuitive adjustments available for Timeout, Auto-On, and Activity settings

-Supports advanced occupancy features, such as dependent occupancy groups and customizable occupied/unoccupied presets in some systems

-Refer to product specification submittal of receiving device to determine system limits

        - Ceiling-Mounted Sensors:  Programmable to operate as an occupancy sensor (automatic-on and automatic-off), an occupancy sensor with low light feature (automatic-on when less than one footcandle of ambient light available and automatic-off), or a vacancy sensor (manual-on and automatic-off).

-Wireless occupancy sensor has two settings available: Auto-On/Auto-Off, and Manual-On/Auto-Off

-Simple and intuitive adjustments available for Timeout, Activity, and Auto-On settings

-Supports advanced occupancy features, such as dependent occupancy groups and customizable occupied/unoccupied presets in some systems

-Refer to product specification submittal of receiving device to determine system limits

        - Wall-Mounted Sensors:  Programmable to operate as an occupancy sensor (automatic-on and automatic-off), or a vacancy sensor (manual-on and automatic-off).

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

Wireless ceiling-mounted occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology for sensing fine motion. Sensor can be auto-on/auto-off, auto-on low light/auto-off, or manual on/auto-off. Ceiling-mounted sensors are recommended for spaces with ceilings less than 12 feet high.

          - <<Type _____ - >>Ceiling-Mounted Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OCR2B-P-WH: Coverage from 324 square feet (30.2 sq m) to 676 square feet (62.4 sq m) depending on ceiling height from 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

Wireless 180 degree coverage wall-mount occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Wall-Mounted Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OWLB-P-WH: Minor motion coverage of 1500 square feet (139.4 sq m) and major motion coverage of 3000 square feet (278.7 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 180 degree field of view.

Wireless 90 degree coverage corner-mount occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Corner-Mounted Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OKLB-P-WH: Minor motion coverage of 1225 square feet (113.8 sq m) and major motion coverage of 2500 square feet (232.3 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 90 degree field of view.

Wireless hallway occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Hallway Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OHLB-P-WH: Major motion coverage of up to 150 feet (45.7 m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); narrow field of view.

      - Wireless Vacancy-Only Sensors:

Visit www.lutron.com for more information on California Title 24 requirements.

        - Operates only as a vacancy sensor (manual-on and automatic-off) )<< in accordance with CAL TITLE 24 P6 requirements>>.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

Wireless ceiling-mounted vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology for sensing fine motion. Sensor is manual on/auto-off (meets California Title 24 requirements). Ceiling-mounted sensors are recommended for spaces with ceilings less than 12 feet high.

          - <<Type _____ - >>Ceiling-Mounted Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VCR2B-P-WH: Coverage from 324 square feet (30.2 sq m) to 676 square feet (62.4 sq m) depending on ceiling height from 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

Wireless 180 degree coverage wall-mount vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Wall-Mounted Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VWLB-P-WH: Minor motion coverage of 1500 square feet (139.4 sq m) and major motion coverage of 3000 square feet (278.7 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 180 degree field of view.

Wireless 90 degree coverage corner-mount vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Corner-Mounted Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VKLB-P-WH: Minor motion coverage of 1225 square feet (113.8 sq m) and major motion coverage of 2500 square feet (232.3 sq m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); 90 degree field of view.

Wireless hallway vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Hallway Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VHLB-P-WH: Major motion coverage of up to 150 feet (45.7 m) with mounting height of 6 to 8 feet (1.8 to 2.4 m); narrow field of view.

    - Radio Window Sensors:

      - Product(s):

        - Lutron Radio Window Sensor; Model LRF2-SSM-XX (mullion mount sensor pair).

        - Lutron Radio Window Sensor; Model LRF2-SSW-WH (window mount).

      - Monitors exterior light conditions and can provide automatic override of system on dark cloudy days or in the presence of shadows from neighboring buildings and rooftop mechanical equipment.

      - During dark conditions, shades and lights can go to predetermined dark override position to maximize view and available daylight.

      - Monitors exterior light conditions and can provide automatic override of system during excessive brightness.

      - During excessive bright conditions, shades and lights can go to predetermined bright override position to maximize occupant comfort.

      - Response rates to light level changes are adjustable via the programming software.

      - Capable of having one or multiple sensors per facade for more localized detection of exterior light conditions.

      - Capable of having one sensor control one shade group or multiple shade groups.

      - Sensor to not require external power packs, power wiring, or communication wiring.

      - Sensor to be easily mountable to mullion (mullion mount sensor pair) or window (window mount) and can be easily removed and repositioned without marring or damaging surface.

      - Provides typical battery lifetime of 10 years when installed per manufacturer instructions.

      - Communicates directly to compatible Lutron QS sensor module via Lutron Clear Connect Technology to ensure reliable RF communications.

      - RF Frequency: 434 MHz.

      - RF Range: 30 feet (9 m) through between sensor and compatible RF receiving device(s).

      - Intuitive test mode to provide instant system verification of associated shades and programmed visor position.

  - ACCESSORIES

    - Emergency Lighting Interface:

Lutron's Application Note #106 contains more information on emergency lighting systems.

      - Product:  Lutron Model LUT-ELI.

      - Senses all three phases of building power.

      - Provides an output to power panels or digital ballast interfaces if power on any phase fails and sends all lights controlled by these devices to <<an emergency light level setting; 100 percent intensity; or __________>>. Lights to return to their previous intensities when normal power is restored.

      - Accepts a contact closure input from a fire alarm control panel.

    - Provide locking covers for controls <<where indicated; located _________; or __________>>.

      - Reversible to allow lock to be located on either side of control.

      - Compatible with IR controls.

      - Does not reduce specified IR range by more than 50 percent of its original specification.

      - Product(s):

        - 1-gang device for compatible Lutron QS keypads; Lutron Model GRX-1GLC.

        - 4-gang device for Lutron Grafik Eye QS preset controls with zone override; Lutron Model QSG-4GLC.

    - Synthetic Minimum Load; Lutron Model LUT-LBX:  Provide as indicated or as required to control loads below dimmer’s minimum rating.

    - Panel Link Translator:

      - Product: Lutron Model HQ-MI-LX.

      - Provides interface for dimmer modules, switching modules, and dimmer cards to communicate on QS link.

      - Enables existing Homeworks Illumination, HomeWorks Interactive, and HomeWorks QS installations with legacy panels to be upgraded to HomeWorks QSX.

      - Supports SENSE wire applications.

    - Power Supplies: Provide power supplies as indicated or as required to power system devices and accessories.

      - Product(s):

        - Din rail-mounted power supply for Lutron HomeWorks QSX processor, system devices, and interfaces with two wire harnesses pre-installed for installation inside a processor panel; Lutron Model QSPS-DH-1-75-H.

        - Din rail-mounted power supply for Lutron HomeWorks QSX processor, system devices, and interfaces with two wire harnesses pre-installed for installation inside a processor panel; Lutron Model WQSPS-DH-1-75-H; TAA – Trade Agreement Act compliant.

        - Din rail-mounted power supply for Lutron HomeWorks system devices, and interfaces for installation in an IP 20 rated consumer panel or breaker panel integrated DIN; Lutron Model QSPS-DH-1-75.

        - Din rail-mounted power supply for Lutron HomeWorks system devices, and interfaces for installation in an IP 20 rated consumer panel or breaker panel integrated DIN; Lutron Model WQSPS-DH-1-75; TAA – Trade Agreement Act compliant.

        - Kit for providing power connection and mounting for up to two Lutron Model QSPS-DH-1-75-H/WQSPS-DH-1-75-H DIN rail-mounted power supplies; Lutron Model PNL-8-PWRKIT HomeWorks PowerKit; with input power switch.

        - Junction box-mounted power supply for shades, keypads, and accessories, and for providing additional low voltage power to communication link; Lutron Model QSPS-J-1-35V; with miswire and thermal protection.

        - Plug-in power supply for shades, drapery drive units, keypads, and accessories, and for providing additional low voltage power to communication link; Lutron Model QSPS-P1-1-35V; with miswire protection; powered from standard receptacle using cord 6 feet (1.8 m) in length; complies with DOE Level VI regulation.

        - Ten output power supply panel for shades, drapery drive units, keypads and accessories, and for providing additional low voltage power to communication link; Lutron Model QSPS-10PNL; no replaceable fuses required for overload/miswire protection; contains DOE Level VI Compliant power supplies.

    - Low-Voltage Enclosures:  Provide as required to house system components.

      - Provide self-contained enclosed area for 120 V power feed.

      - Product(s):

        - Lutron Model LV14; 14 inches (35.6 cm) high, nominal; surface mounting; for mounting one processor or one system interface and up to two wire landing boards.

        - Lutron Model LV21; 21 inches (53.3 cm) high, nominal; surface or flush mounting; for mounting up to two processors or up to two system interfaces and up to five wire landing boards.

    - Wire Landing Boards; Lutron Model QS-WLB:  Provide as indicated or as required for terminating wiring.

  - SOURCE QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - Factory Testing; Lutron Standard Factory Testing:

To ensure that 100 percent of the lighting control products work at installation, the manufacturer should test 100 percent of all assemblies at full rated load in the factory. This testing will assure that every product has been tested and guaranteed to work. Sampling would only prove that the samples work and should not be acceptable.

      - Perform full-function factory testing on all completed assemblies. Statistical sampling is not acceptable.

To ensure that 100 percent of the lighting control products work at installation, the manufacturer should test 100 percent of LED drivers at the factory.

      - Perform full-function factory testing on 100 percent of all LED drivers.

Audit burn-in is used to verify the consistency of quality for the supplied devices and manufacturing processes so that they meet the design intent.

      - Perform factory audit burn-in of all dimming assemblies at 104 degrees F (40 degrees C) at full load for two hours.

Sample burn-in is used to verify the consistency of quality for the supplied devices and manufacturing processes so that they meet the design intent.

- EXECUTION

  - EXAMINATION

    - Verify that field measurements are as shown on the drawings.

    - Verify that ratings and configurations of system components are consistent with the indicated requirements.

    - Verify that mounting surfaces are ready to receive system components.

    - Verify that conditions are satisfactory for installation prior to starting work.

  - INSTALLATION

    - Perform work in a neat and workmanlike manner in accordance with NECA 1 and, where applicable, NECA 130<<, except for mounting heights specified in those standards;, including mounting heights specified in those standards unless otherwise indicated; or __________>>.

    - Install products in accordance with manufacturer's instructions.

In order for the system to be fully commissioned and operating to specification, a database will need to be created. It is critical that the manufacturer receive information on load and control functionality so that the database can be written and fully tested by the manufacturer.

    - Define each dimmer/relay load type, assign each load to a zone, and set control functions.

    - Sensor locations indicated are diagrammatic. Within the design intent, reasonably minor adjustments to locations may be made in order to optimize coverage and avoid conflicts or problems affecting coverage, in accordance with manufacturer's recommendations.

In order for the exterior daylight sensor to respond to daylight during the entire daylight period, the sensor should face north so that in the morning it will see daylight from the east and in the evening it will see daylight from the west. Directing the sensor due north also minimizes direct lighting exposure to the sensor which could overload the sensor.

    - Mount exterior daylight sensors to point due north with constant view of daylight.

Interior sensors work mainly with diffused light, as such, they have a much higher lighting gain than exterior sensors. Electric light sources can affect these sensors unless the sensors are shielded from the light given off by electric light sources.

    - Ensure that daylight sensor placement minimizes sensor view of electric light sources. Locate ceiling-mounted and luminaire-mounted daylight sensors to avoid direct view of luminaires.

If the lamp leads exceed the specification, trouble starting the lamps may result.

    - LED Light Engine/Array Lead Length: Do not exceed 100 feet (31 m).

    - Identify system components << in accordance with Section 26 0553>>.

  - FIELD QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - System Startup:

      - Residential System Provider to conduct minimum of three site visits to ensure proper system installation and operation.

      - Conduct Pre-Installation visit to review requirements with installer as specified in Part 1 under "Administrative Requirements".

      - Conduct second site visit upon completion of lighting control system to perform system startup and verify proper operation:

        - Verify connection of power wiring and load circuits.

        - Verify connection and location of controls.

        - Energize lighting control system processors and download system data program.

        - Address devices.

        - Verify system operation control by control.

        - Verify proper operation of manufacturer's interfacing equipment.

        - Configure initial groupings of ballast for wall controls, daylight sensors and occupancy sensors.

        - Provide initial rough calibration of sensors; fine-tuning of sensors is responsibility of Contractor.

        - Train Owner's representative on system capabilities, operation, and maintenance, as specified in Part 3 under "Closeout Activities".

        - Obtain sign-off on system functions.

      - Conduct third site visit to make required light adjustments to the system for conformance with original design intent.

    - Correct defective work, adjust for proper operation, and retest until entire system complies with contract documents.

  - CLEANING

    - Clean exposed surfaces to remove dirt, paint, or other foreign material and restore to match original factory finish.

  - COMMISSIONING

    - See Section 01 9113 – General Commissioning Requirements for commissioning requirements.

Use the following paragraph to specify that lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) be performed by Lighting Control Manufacturer. Edit the second choice to have this additional cost included as an alternate or as part of the base bid.

Required documentation associated with this service is also specified in Part 1 under “SUBMITTALS”.

    - Title 24 Acceptance Testing Service; Lutron LSC-SPV-DOC-T24: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to perform lighting control acceptance testing in accordance with CAL TITLE 24 P6. Submit required documentation.

  - CLOSEOUT ACTIVITIES

    - See Section 01 7800 - Closeout Submittals, for closeout submittals.

    - See Section 01 7900 - Demonstration and Training, for additional requirements.

    - Residential System Provider to perform on-site training of Owner's personnel on operation, adjustment, and maintenance of lighting control system.

  - PROTECTION

    - Protect installed products from subsequent construction operations.

END OF SECTION