SECTION 260995

HOTEL GUESTROOM CONTROLS - LUTRON MYROOM

This section includes guestroom lighting, temperature, and shade/drapery controls featuring basis of design products from Lutron Electronics Company, Inc. The section also includes motorized drapery track specifically designed for hotel guestroom applications and for integration with the specified system. Motorized shades that may also be controlled by this system are specified in Section 12 2400 (12490) - Window Shades – Lutron Sivoia QS/Sivoia QS Wireless or Section 12 2400 (12490) – Window Shades – Lutron Contract Roller.

Because of the complex nature of this type of system, it is recommended that the specification and drawings be closely coordinated with consultation from the basis of design manufacturer. If systems of other manufacturers are listed or considered for substitution, the specifier should conduct a thorough evaluation to ensure that the system provides equivalent performance and that other related products will interface properly.

SECTION 26 0995 (16595) – HOTEL GUESTROOM CONTROLS – LUTRON MYROOM, Copyright 2014-2021, Lutron Electronics Company, Inc.

- GENERAL

  - SECTION INCLUDES

    - Hotel guestroom control system and associated components:

      - Load control modules.

      - Guestroom control units.

      - Guestroom control system software.

      - Radio frequency (RF) repeaters.

      - Control stations.

      - Preset controls with zone override.

      - Room thermostats.

      - Wired sensors.

      - Wireless sensors.

      - Low-voltage control interfaces.

      - Power interfaces.

      - LED drivers.

      - Control system accessories.

    - Motorized drapery track and associated accessories.

  - RELATED REQUIREMENTS

Include the following paragraph only if specifying motorized window treatments.

    - Section 06 1000 - Rough Carpentry: Concealed wood blocking for attachment of window treatment brackets.

Include the following paragraph only if specifying motorized window treatments.

    - Section 09 2116 - Gypsum Board Assemblies: Substrate for window treatments.

Include the following paragraph only if motorized shades are to be controlled by the guestroom control system.

    - Section 12 2400 - <<Window Shades – Lutron Sivoia QS/Sivoia QS Wireless; Window Shades – Lutron Contract Roller>>: Motorized roller window shades, for interface with guestroom control system.

    - Section <<______>>: Building automation system, for interface with guestroom control system.

    - Section 26 0553 - Identification for Electrical Systems:  Identification products and requirements.

    - Section 26 2726 - Wiring Devices - Lutron:

      - Finish requirements for wall controls specified in this section.

      - Accessory receptacles and wall plates, to match guestroom controls specified in this section.

    - Section 26 5133 - Luminaires, Ballasts, and Drivers – Lutron.

  - REFERENCE STANDARDS

    - 47 CFR 15 – Radio Frequency Devices; current edition.

    - ANSI C82.11 - American National Standard for Lamp Ballasts - High Frequency Fluorescent Lamp Ballasts - Supplements; 2011.

    - ANSI/ESD S20.20 - Protection of Electrical and Electronic Parts, Assemblies and Equipment (Excluding Electrically Initiated Explosive Devices); 2014.

    - ASTM D4674 - Standard Practice for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Office Environments; 2002a (Reapproved 2010).

    - ASTM E308 - Standard Practice for Computing the Colors of Objects by Using the CIE System; 2017.

    - CAL TITLE 24 P6 – California Code of Regulations, Title 24, Part 6 (California Energy Code); 2013.

    - CSA C22.2 No. 223 – Power Supplies with Extra-low-voltage Class 2 Outputs; 2015.

    - IEC 60669-2-1 - Switches for Household and Similar Fixed Electrical Installations - Part 2-1: Particular Requirements - Electronic Switches; 2015.

    - IEC 60929 - AC and/or DC-Supplied Electronic Control Gear for Tubular Fluorescent Lamps - Performance Requirements; 2015.

    - IEC 61000-4-2 - Electromagnetic Compatibility (EMC) - Part 4-2: Testing and Measurement Techniques - Electrostatic Discharge Immunity Test; 2008.

    - IEC 61000-4-5 - Electromagnetic Compatibility (EMC) - Part 4-5: Testing and Measurement Techniques - Surge Immunity Test; 2014, with Amendments, 2017.

    - IEEE 1789 - Recommended Practice for Modulating Current in High-Brightness LEDs for Mitigating Health Risks to Viewers; 2015.

    - IEEE C62.41.2 - Recommended Practice on Characterization of Surges in Low-Voltage (1000 V and less) AC Power Circuits; 2002 (Cor 1, 2012).

    - ISO 9001 - Quality Management Systems-Requirements; 2008.

    - NECA 1 - Standard for Good Workmanship in Electrical Construction; 2015.

    - NECA 130 - Standard for Installing and Maintaining Wiring Devices; National Electrical Contractors Association; 2010.

    - NEMA 410 - Performance Testing for Lighting Controls and Switching Devices with Electronic Drivers and Discharge Ballasts; National Electrical Manufacturers Association; 2015.

    - NEMA SSL 7A – Phase Cut Dimming for Solid State Lighting: Basic Compatibility; 2015.

    - NEMA WD 1 - General Color Requirements for Wiring Devices; National Electrical Manufacturers Association; 1999 (R 2015).

    - NFPA 70 - National Electrical Code; National Fire Protection Association; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.

    - NFPA 701 - Standard Methods of Fire Tests for Flame Propagation of Textiles and Films; 2015.

    - UL 94 - Tests for Flammability of Plastic Materials for Parts in Devices and Appliances; Current Edition, Including All Revisions.

    - UL 924 - Emergency Lighting and Power Equipment; Current Edition, Including All Revisions.

    - UL 1310 – Class 2 Power Units; Current Edition, Including All Revisions.

    - UL 1598C - Light-Emitting Diode (LED) Retrofit Luminaire Conversion Kits; Current Edition, Including All Revisions.

    - UL 2043 - Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces; Current Edition, Including All Revisions.

    - UL 8750 - Light Emitting Diode (LED) Equipment for Use in Lighting Products; Current Edition, Including All Revisions.

  - ADMINISTRATIVE REQUIREMENTS

    - Coordination:

      - Coordinate the placement of sensors and wall controls with millwork, furniture, equipment, etc. installed under other sections or by others.

      - Coordinate the placement of wall controls with actual installed door swings.

      - Coordinate the work to provide luminaires and lamps compatible with the lighting controls to be installed.

      - Where door lock system integration is indicated, coordinate the work with other trades to provide compatible products.

      - Notify Architect of any conflicts or deviations from the contract documents to obtain direction prior to proceeding with work.

    - Pre-Wire Meeting:  Conduct on-site meeting with Lighting Control Manufacturer prior to commencing work as part of manufacturer's system mock-up and full-scope startup services as applicable. Manufacturer to review with installer:

      - Low voltage wiring requirements.

      - Separation of power and low voltage/data wiring.

      - Wire labeling.

      - Guestroom control unit locations and installation.

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS".

      - Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS", sensor locations to be reviewed in accordance with layout provided by Lighting Control Manufacturer. Lighting Control Manufacturer may direct Contractor regarding sensor relocation should conditions require a deviation from locations indicated.

      - Control locations.

      - Load circuit wiring.

      - Network wiring requirements.

      - Connections to other equipment.

      - Installer responsibilities.

    - Sequencing:

Include the following paragraph only if specifying motorized window treatments.

      - Do not fabricate window treatments until field dimensions for each opening have been taken.

Include the following paragraph only if specifying motorized window treatments.

      - Do not install window treatments until final surface finishes and painting are complete.

      - Do not install sensors and wall controls until final surface finishes << and painting>> are complete.

  - SUBMITTALS

    - See Section 01 3000 - Administrative Requirements for submittal procedures.

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS".

    - Design Documents: Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS", Lighting Control Manufacturer to provide plans indicating occupancy/vacancy sensor locations.

    - Product Data:

      - Guestroom Control System Components:  Include ratings, configurations, standard wiring diagrams, dimensions, colors, service condition requirements, and installed features.

      - Occupancy/Vacancy Sensors:  Include detailed motion detection coverage range diagrams.

Include the following paragraph only if specifying motorized window treatments.

      - Motorized Window Treatments:  Include materials, finishes, fabrication details, dimensions, profiles, and mounting requirements.

    - Shop Drawings:

      - Provide load schedule indicating actual connected load, load type, and voltage per circuit, circuits and their respective control zones, and capacity, phase, and corresponding circuit numbers.

      - Provide schematic system riser diagram indicating component interconnections. Include requirements for interface with other systems.

Include the following paragraph only if specifying motorized window treatments.

      - Motorized Window Treatments:  Include <<window treatment schedule indicating size, location and keys to details; head, jamb and sill details; mounting dimension requirements for each product and condition; operation direction; and __________>>.

    - Certificates: Manufacturer's documentation that line voltage components are UL listed or UL recognized.

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatment Test Reports: Indicating compliance with specified fabric properties.

    - Samples:

      - Wall Controls:

        - Show available color and finish selections.

        - Provide <<one; or _____>> sample(s) for each product << proposed for substitution; or __________>><< upon request; or __________>>.

      - Sensors:  Provide <<one; or _____>> sample(s) for each product << proposed for substitution; or __________>><< upon request; or __________>>.

Include the following paragraph only if specifying motorized window treatments.

      - Window Treatment Fabric: Showing <<specified colors and patterns; manufacturer's full range of available colors and patterns; or _________>>.

    - Manufacturer's Installation Instructions:  Include application conditions and limitations of use stipulated by product testing agency. Include instructions for storage, handling, protection, examination, preparation, and installation of product.

Use the following paragraph to specify system performance-verification documentation (at an additional cost). System Performance-Verification Documentation is often required for LEED projects, projects which involve a commissioning agent, or Title 24 (California) projects. Edit the second choice to have this additional cost included as an alternate or as part of the base bid. This documentation will be completed by a Lutron Services Company Representative during the startup of the guestroom control system. This documentation defines the functional test procedures to be used and the results of the onsite testing of the Lutron equipment. A copy of this documentation will be delivered after startup completion.

    - System Performance-Verification Documentation; Lutron LSC-SPV-DOC: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's enhanced documentation detailing start-up performance-verification procedures and functional tests performed along with test results.

Include the following paragraph if lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) is specified in Part 3 under "COMMISSIONING".

    - Title 24 Acceptance Testing Documentation:  Submit Certification of Acceptance and associated documentation for lighting control acceptance testing performed in accordance with CAL TITLE 24 P6, as specified in Part 3 under “COMMISSIONING”.

    - Project Record Documents:  Record actual installed locations and settings for lighting control system components.

    - Operation and Maintenance Data:  Include detailed information on guestroom control system operation, equipment programming and setup, replacement parts, and recommended maintenance procedures and intervals.

    - Warranty: Submit sample of manufacturer's Warranty or Enhanced Warranty as specified in Part 1 under "WARRANTY". Submit documentation of final execution completed in Owner's name and registered with manufacturer.

Include the following paragraph only if post-occupancy maintenance is to be included in this contract. See article "MAINTENANCE" under Part 3.

    - Maintenance contracts.

  - QUALITY ASSURANCE

    - Conform to requirements of NFPA 70.

    - Maintain at the project site a copy of each referenced document that prescribes execution requirements.

    - Manufacturer Qualifications:

      - Company with not less than ten years of experience manufacturing lighting control systems of similar complexity to specified system.

      - Registered to ISO 9001, including in-house engineering for product design activities.

      - Qualified to supply specified products and to honor claims against product presented in accordance with warranty.

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatment Installer Qualifications: Qualified to install and commission specified products by prior factory training, experience, demonstrated performance, and acceptance of any requirement of the manufacturer, subsidiary of the manufacturer, or licensed agent.

Include the following paragraph if lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) is specified in Part 3 under "COMMISSIONING".

    - Title 24 Acceptance Testing Technician Qualifications:  Certified by a California approved Acceptance Test Technician Certification Provider as an Acceptance Test Technician (ATT) in accordance with CAL TITLE 24 P6.

Include the following paragraph only if post-occupancy maintenance is to be included in this contract, or if proposals for maintenance under another contract are being solicited in these contract documents. See article "MAINTENANCE" under Part 3.

    - Maintenance Contractor Qualifications:  Manufacturer's authorized service representative.

  - MOCK-UP

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatment Mock-Up: Provide<< full size; minimum 2 ft wide by 3 ft high ( minimum 0.60 m wide by 0.94 m high); minimum __ ft wide by __ ft high ( minimum __ m wide by __ m high);or  ______>> mock-up of window treatment complete with selected materials.

Definitions of light and privacy characteristics of fabrics are not precise. If critical, view the actual fabric under the light conditions expected. A mock-up would be useful for this purpose but it would probably be better to do this evaluation before taking bids.

      - Obtain Architect's approval of light and privacy characteristics of fabric prior to fabrication.

--CHOOSE ONE OF THE TWO PARAGRAPHS BELOW--

      - Full-sized mock-up may become part of the final installation.

      - Full-sized mock-up will become the property of the Owner to be used for spare parts.

    - Manufacturer's System Mockup Services; Lutron LSC-MYRM-MOCK myRoom Prime/Plus System Mockup:

      - Manufacturer's authorized Service Representative to conduct minimum of two site visits to ensure proper system mockup installation and operation.

      - Conduct Pre-Wire visit to review requirements with installer as specified in Part 1 under "Administrative Requirements".

      - Conduct second site visit upon completion of system mockup installation to perform system startup and verify proper operation as required for mockup approval.

  - Train Owner's representative on system capabilities, operation, and DELIVERY, STORAGE, AND HANDLING

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatments:  Deliver components in manufacturer's unopened packaging, labeled to identify each window treatment for each opening.

    - Store products in a clean, dry space in accordance with manufacturer's written instructions until ready for installation.

  - FIELD CONDITIONS

    - Maintain field conditions within manufacturer's required service conditions during and after installation.

      - Basis of Design System Requirements - Lutron, Unless Otherwise Indicated:

        - Ambient Temperature:  Between 32 and 104 degrees F (0 and 40 degrees C).

        - Relative Humidity:  Less than 90 percent, non-condensing.

During the installation phase, considerable dust (drywall, concrete, etc) may be deposited on electrical components and impair performance. General accepted housekeeping protection of the electrical equipment must be maintained.

        - Protect against accumulation or infiltration of dust.

  - WARRANTY

    - See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

Lutron Standard 2-Year Warranty coverage includes:

-100 percent parts and labor coverage for first two years for guestroom control system components, except ballasts/drivers.

-First-available on-site or remote response time.

-Telephone technical support; 24 hours per day, 7 days per week, excluding manufacturer holidays.

Consider including an optional Enhanced Warranty below.

    - Guestroom Control System Manufacturer's Standard Warranty, With Manufacturer Start-Up; Lutron Standard 2-Year Warranty; Lutron LSC-B2:

      - Manufacturer Guestroom Control System Components, Except Ballasts/Drivers:

        - First Two Years:

          - 100 percent replacement parts coverage, 100 percent manufacturer labor coverage to troubleshoot and diagnose a lighting issue.

          - First-available on-site or remote response time.

          - Remote diagnostics for applicable systems.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

      - Ballasts/Drivers: Five years 100 percent parts coverage, no manufacturer labor coverage.

Use one of the three following paragraphs to specify an optional Enhanced Warranty. Edit the choice to have this additional value included as an alternate or as part of the base bid.

Lutron Silver Enhanced Warranty includes standard 2-year warranty coverage plus:

-Upgrade to 8-year limited parts warranty coverage for guestroom control system components, excluding ballasts/drivers.

Lutron Gold Enhanced Warranty includes standard 2-year warranty coverage plus:

-Upgrade to 8-year limited parts warranty coverage for guestroom control system components, excluding ballasts/drivers.

-Upgrade to 72-hour on-site or remote response time.

-Annual scheduled Preventative Maintenance Visit.

Lutron Platinum Enhanced Warranty includes standard 2-year warranty coverage plus:

-Upgrade to 8-year limited parts warranty coverage for guestroom control system components, excluding ballasts/drivers.

-Upgrade to 24-hour on-site or remote response time.

-Annual scheduled Preventative Maintenance Visit.

--CHOOSE ONLY ONE OF THE THREE OPTIONAL CONTROL SYSTEM ENHANCED WARRANTIES BELOW--

    - Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's Guestroom Control System Enhanced Warranty with manufacturer Start-up; Silver Enhanced Warranty; Lutron LSC-E8S; coverage to include items listed under manufacturer's standard warranty with manufacturer start-up above, plus the following upgrades:

      - Manufacturer Guestroom Control System Components, Except Ballasts/Drivers and Ballast Modules:

        - First Two Years:

          - As-available Field Service response; no committed response time.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

    - Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's Guestroom Control System Enhanced Warranty with manufacturer Start-up; Gold Enhanced Warranty; Lutron LSC-E8G; coverage to include items listed under manufacturer's standard warranty with manufacturer start-up above, plus the following upgrades:

      - Manufacturer Guestroom Control System Components, Except Ballasts/Drivers and Ballast Modules:

        - First Two Years:

          - Upgrade from as-available Field Service response to 72-hour on-site or remote response time.

          - Plus annual scheduled Preventive Maintenance Visit.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

    - Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for manufacturer's Guestroom Control System Enhanced Warranty with manufacturer Start-up; Platinum Enhanced Warranty; Lutron LSC-E8P; coverage to include items listed under manufacturer's standard warranty with manufacturer start-up above, plus the following upgrades:

      - Manufacturer Guestroom Control System Components, Except Ballasts/Drivers and Ballast Modules:

        - First Two Years:

          - Upgrade from as-available Field Service response to 24-hour on-site or remote response time.

          - Plus annual scheduled Preventive Maintenance Visit.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

Include the following paragraph only if specifying motorized window treatments.

    - Motorized Window Treatment Manufacturer's Warranty; Lutron 8-Year Limited Warranty:

      - Window Treatment Components (including electronic drive units, fabric, and hardware):

        - Years 1-5: 100 percent replacement parts coverage, no manufacturer labor coverage.

        - Years 6-8: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

- PRODUCTS

  - MANUFACTURERS

Use the choice in the paragraph below to specify myRoom plus or myRoom prime according to project requirements. Visit www.lutron.com for a comparison of systems.

    - Basis of Design Manufacturer:  Lutron Electronics Company, Inc; <<myRoom plus; myRoom prime; or _________>>; www.lutron.com.

    - Other Acceptable Manufacturers:

      - <<______>>.

      - Products by listed manufacturers are subject to compliance with specified requirements<< and prior approval of Architect; or _________>>.

    - Substitutions:  <<See Section 01 6000 - Product Requirements; Not permitted; or __________>>.

Delete the following three subparagraphs if substitutions are not permitted.

      - All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by Architect a minimum of <<10; or _____>> working days prior to the bid date and must be made available to all bidders. Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

      - Any proposed substitutions to be reviewed by Architect at Contractor's expense << at a rate of $200 per hour; at a rate of _________; or __________>>.

      - By using pre-approved substitutions, Contractor accepts responsibility and associated costs for all required modifications to related equipment and wiring. Provide complete engineered shop drawings (including power wiring) with deviations from the original design highlighted in an alternate color for review and approval by Architect prior to rough-in.

    - Source Limitations:  Furnish products produced by a single manufacturer and obtained from a single supplier.

  - GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS

--CHOOSE ONLY ONE OF THE TWO SENSOR LAYOUT AND TUNING PARAGRAPHS BELOW--

Use the following paragraph to specify optional manufacturer Sensor Layout and Tuning service or use the paragraph below if Lighting Control Manufacturer Sensor Layout and Tuning service will not be provided. Edit the choice to have this additional value included as an alternate or as part of the base bid.

    - Sensor Layout and Tuning:  Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer's Sensor Layout and Tuning service; Lutron LSC-SENS-LT:

      - Lighting Control Manufacturer to take full responsibility for wired or wireless sensor layout and performance for sensors provided by Lighting Control Manufacturer.

      - Lighting Control Manufacturer to analyze the reflected ceiling plans, via supplied electronic AutoCAD format, and design a detailed sensor layout that provides adequate occupancy sensor coverage and ensures occupancy sensor performance per agreed upon sequence of operations. Contractor to utilize the layouts for sensor placement.

      - During startup, Lighting Control Manufacturer to direct Contractor regarding sensor relocation, as required, should conditions require a deviation from locations specified in the drawings.

      - Lighting Control Manufacturer to provide up to two additional post-startup on-site service visits within one calendar year from Date of Substantial Completion to fine-tune sensor calibration per the agreed upon sequence of operations.

Use the following paragraph if Lighting Control Manufacturer Sensor Layout and Tuning service will not be provided, or use the paragraph above to specify optional manufacturer Sensor Layout and Tuning service.

    - Sensor Layout and Tuning:  No Lighting Control Manufacturer Sensor Layout and Tuning service to be provided; Lutron LSC-NO-SENS-LT.

      - Contractor to utilize Lighting Control Manufacturer Installation Instructions to place/install sensors.

      - At Pre-wire and Startup, Lighting Control Manufacturer to provide a rough sensor calibration only. Sensor fine-tuning to be the responsibility of Contractor.

    - Provide products listed, classified, and labeled by Underwriter's Laboratories Inc. (UL) as suitable for the purpose indicated.

    - Unless specifically indicated to be excluded, provide all required equipment, conduit, boxes, wiring, connectors, hardware, supports, accessories, software, system programming, etc. as necessary for a complete operating system that provides the control intent indicated.

    - Guestroom Control Requirements:

      - Capable of initiating defined sequence of operations based on:

        - Occupied/Unoccupied status.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

        - Guestroom sold/unsold status (with Property Management System integration).

        - Guest manual control.

      - Guest Presence Detection Algorithm:

        - Determine presence of guest(s) in the room using algorithm that considers status of both occupancy/vacancy sensor(s) and door input.

        - If output of algorithm indicates that guest(s) have left the room, transition room to unoccupied status and take appropriate programmed actions.

        - If output of algorithm indicates that guest(s) have occupied the room, transition the room to occupied status and take appropriate programmed actions.

        - Capable of assigning additional timeout through system programming.

      - Welcome Scenes:

        - Capable of assigning a default welcome scene.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

        - Capable of assigning multiple welcome scenes (e.g. guest first entry, guest subsequent entry, staff entry) that respond to programmed doorlock integration using compatible products.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - Turndown Service Scene:

        - Capable of assigning a scene that sets lighting, shades, and temperature with a single button to pre-programmed levels ready for the guest after the turndown service of the room has occurred.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - Privacy/Service:  Capable of control/indication of make-up-room and do-not-disturb requests.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - Capable of integration (using specified software) with:

        - Property Management System.

        - Building Management System (via BACnet IP).

        - Door Lock System.

Include the following paragraph only if specifying motorized window treatments with digital communications link (wired or wireless).

      - Window Treatments With Digital Communications Link (Wired or Wireless):

Include the optional choice in the following paragraph for myRoom plus systems only (only keypad for myRoom prime).

        - Capable of operating window treatments and recalling presets via keypad<<, guestroom control system software, or other guestroom control system interface>>.

        - Capable of operating any individual, group, or subgroup of window treatment electronic drive units within system without requiring separate group controllers.

        - Capable of assigning and reassigning individual, groups, and subgroups of window treatments to any control within system without requiring additional wiring or hardware changes.

        - Capable of controlling window treatment speed for tracking within plus or minus 0.125 inch (3.17 mm) throughout entire travel.

        - Provide 10 year power failure memory for preset stops, open and close limits, window treatment grouping and sub grouping and system configuration.

        - Capable of synchronizing multiple window treatment electronic drive units to start, stop, and move in unison.

        - Capable of stopping window treatments within accuracy of 0.125 inch (3.17 mm) at any point between open and close limits.

        - Capable of storing up to 250 programmable stop points, including open, close, and any other position.

        - Capable of controlling lights and window treatments from single wall control button.

        - Open and close limits programmable from electronic drive unit or keypad.

Include the following paragraph only if specifying motorized window treatments without digital communications link.

      - Window Treatments Without Digital Communications Link:

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

        - Guestroom Control System Integration:  Capable of operating window treatments via contact closure input from contact closure interface.

        - Standalone Operation:  Capable of operating window treatments via contact closure input from standalone keypad.

Typical dimming equipment is rated for 40 degrees C (104 degrees F). This is the maximum ambient temperature that can exist while the dimming equipment is operating at full load conditions. Include the following paragraph to ensure that the operating equipment is designed to operate at worst case environmental conditions without affecting product life.

    - Design lighting control equipment for 10 year operational life while operating continually at any temperature in an ambient temperature range of 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C) and 90 percent non-condensing relative humidity.

    - Electrostatic Discharge Tolerance: Design and test equipment to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

Power dropouts occur frequently. When power is restored, the lighting system should recover quickly and automatically return to the last lighting levels. A momentary interruption (1 or 2 seconds) of power should not cause extended periods (20 seconds or more) without lighting while the system reboots and all other electrical equipment is back on.

    - Power Failure Recovery: When power is interrupted and subsequently restored, within 3 seconds lights to automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

    - Device Finishes:

      - Wall Controls: <<Match finishes specified for wiring devices in Section 26 2726, unless otherwise indicated; As indicated on the drawings; To be selected by Architect; or __________>>.

      - Standard Colors: Comply with NEMA WD1 where applicable.

      - Color Variation in Same Product Family: Maximum delta E of 1, CIE L*a*b color units per ASTM E308.

Daylight or fluorescent lighting generate ultraviolet light which can cause parts that do not meet ASTM D4674 to discolor/yellow over time.

      - Visible Parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

Use the following paragraph if interface with building automation system will be required. Any specific requirements can be added as subparagraphs below.

    - Interface with building automation system<< as specified in Section _____>>.

    - Interface with Existing Work: <<______>>.

  - LOAD CONTROL MODULES

    - DIN Rail Power Modules:

      - General Requirements:

        - Surge Tolerance: Designed and tested to withstand surges of 6,000 V, 3,000 amps according to IEEE C62.41.2 and IEC 61000-4-5 without impairment to performance.

        - Power:  120-240 VAC, 50/60 Hz; provide connection as indicated or as required.

        - Communications:  Utilize RS485 wiring for low-voltage communications link.

        - Passively cooled via free-convection, unaided by fans or other means.

      - Switching Power Modules:

        - Product(s):

          - <<Type _____ - >>4-zone switching module; Lutron Model MQSE-4S1-D.

          - <<Type _____ - >>3-zone switching module; Lutron Model MQSE-3S1-D.

          - <<Type _____ - >>2-zone switching module; Lutron Model MQSE-2S1-D.

        - Output Zones:  Each zone rated at 1 A for resistive, inductive, or capacitive lighting loads as defined by IEC 60669-2-1 and NEMA 410.

        - Manual Mode Operation:  Provide button for each zone to turn loads on/off.

        - Provide LED indicators for displaying diagnostic information.

        - Contact Closure Input:

Include the optional choice in the following paragraph for myRoom plus systems only (keycard device interface not available with myRoom prime systems).

          - Provides interface for integration with magnetic door switch <<or keycard device>>.

          - Accepts both momentary and maintained contact closures (maintained contact closure required to function correctly from door input).

        - Contact Closure Output:

          - Provides interface for integration with room thermostat (setback control) or to control receptacles (via contactor).

--CHOOSE ONLY ONE OF THE TWO PARAGRAPHS BELOW--

Include the following paragraph for myRoom prime systems.

          - Maintained output.

Include the following paragraph for myRoom plus systems.

          - Can be configured for maintained or pulsed output.

          - Inductive Loads:  Provide flyback diode wired per manufacturer’s instructions to control unclamped inductive loads such as relays, solenoids, and motors.

      - Phase Adaptive Power Modules:

        - Product(s):

          - <<Type _____ - >>4-zone phase adaptive module; Lutron Model MQSE-4A1-D.

          - <<Type _____ - >>3-zone phase adaptive module; Lutron Model MQSE-3A1-D.

          - <<Type _____ - >>2-zone phase adaptive module; Lutron Model MQSE-2A1-D.

        - Output Zones:  Each zone rated for incandescent/halogen (120 W, 120 V), electronic low voltage (120 W, 120 V), magnetic low voltage (120 VA/90 W, 120 V), or neon/cold cathode (120 VA/90 W, 120 V); one load type per zone; minimum 5 W incandescent load requirement.

        - Manual Mode Operation:  Provide button for each zone to turn loads on/off or dim loads up/down.

        - Provide LED indicators for displaying diagnostic information.

        - Provide cycle-by-cycle compensation for incoming line voltage variations, including changes in voltage, frequency shifts, harmonics, and line noise; accommodate up to plus/minus two percent change in frequency per second.

        - Systems not providing cycle-by-cycle compensation to include external power conditioning equipment as part of dimming system.

        - Comply with NEMA SSL 7A.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - Digital Fixture Control Modules:

        - Product:  Lutron Power Module with EcoSystem; Model LQSE-2ECO-D.

        - Provide testing capability using manual override buttons.

        - Provide two low-voltage digital communication links; each link to support up to 64 ballasts or LED drivers capable of NFPA 70 Class 1 or Class 2 installation.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - DALI Fixture Control Modules:

        - Product:  Lutron DALI Power Module; Model QSN-2DALUNV-D.

        - Provide testing capability using manual override buttons.

        - Provide bus power and control for two DALI buses; each DALI bus supports:

          - Control of up to 64 DALI compliant addressable loads, grouped into up to 16 zones.

          - Up to 250 mA bus power.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

  - GUESTROOM CONTROL UNITS

    - Product(s):

      - <<Type _____ - >>2-link control unit; Lutron Model GCU-HOSP.

      - <<Type _____ - >>1-link control unit; Lutron Model GCU-HOSP-1.

    - Power:  Class 2 (low voltage).

    - Communications:

      - Wired Communications:  Utilize RS485 wiring for low-voltage communications links.

        - Each link configurable as a wired device link or wireless link (via wired connection to RF repeater).

        - Each link supports up to 50 devices/zones.

      - Ethernet:  For system start-up and property/building management system integration (with required software licenses).

    - Furnished with astronomical timeclock with minimum accuracy of plus/minus 1 minute per year.

    - Maintains a backup of the programming in a non-volatile memory, with timeclock retention of ten years without power.

    - Terminal block inputs to be over-voltage and miswire-protected against reversals and shorts.

    - Provide LED indicators for displaying diagnostic information.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

  - GUESTROOM CONTROL SYSTEM SOFTWARE

    - Guestroom Control and Monitor Software:

      - Product:  Lutron myRoom Vue.

      - General Requirements:

        - Web-based; runs on most HTML5 compatible browsers (including Internet Explorer, Chrome, and Safari).

        - Supports multiple platforms and devices; runs from a tablet, desktop, or laptop; optimized for displays of 1024 by 768 pixels or higher.

        - User interface supports multi-touch gestures such as pinch to zoom, drag to pan, etc.

        - Utilizes HTTPS (industry-standard certificate-based encryption and authentication for security).

        - All functionality listed below must be available via a single application.

        - Supports up to 1,000 guestrooms.

        - Software capable of monitoring and control of lights, window treatments, and temperature.

      - System Navigation and Status Reporting:

        - Performed using graphical floor plan view or a generic system layout.

        - Graphical Floor Plan View:  Utilizes customized CAD based drawing of the building. Pan and zoom feature allows for easy navigation; dynamically adjusts the details presented based on zoom level.

        - Room Dashboard:  Provides summary of guestroom status with means for accessing more detailed information.

        - Room Properties View:  Lists guestroom properties (e.g. door ajar, check-in/check-out status, etc.) for troubleshooting.

      - Control/Monitor Guestroom Lights:

        - Guestroom lights can be monitored for on/off status or current level.

        - All lights in a guestroom can be turned on/off or sent to a specific level.

        - For guestrooms that have been zoned, these guestrooms may be sent to a predefined lighting scene, and individual zones may be controlled.

        - Guestroom lighting scenes can be renamed and modified in real-time, changing the levels that zones go to when a scene is activated.

        - High and low end of guestroom lighting can be tuned/trimmed.

Include the following paragraph only if specifying motorized window treatments with digital communications link (wired or wireless).

      - Control/Monitor Guestroom Window Treatments:

        - Guestroom window treatments can be monitored for current preset or position.

        - Guestroom window treatments can be opened/closed, sent to a preset, or sent to a specific position.

      - Control/Monitor Guestroom Thermostats:

        - Guestroom thermostats can be monitored for current room temperature, setpoint, and operating mode.

        - Guestroom thermostat setpoint, operating mode, and setbacks can be adjusted.

        - Current and historical HVAC performance can be monitored for troubleshooting. View current temperature, guest set temperature and automation setbacks overlaid with HVAC fan speed, HVAC operating mode and room occupancy.

      - Control/Monitor Guestroom Automation:

        - Guestroom occupancy status, check-in/out status and service/privacy requests can be monitored.

        - Guestroom automation can be enabled/disabled.

      - Reporting: Provide reporting capability that allows the building manager to gather real-time and historical information about the system as follows:

        - Energy Reports: Show a comparison of cumulative energy used over a period of time for one or more areas. Reports include lighting and HVAC energy.

        - Power Reports: Show power usage trend over a period of time for one or more areas. Reports include lighting and HVAC energy.

        - Energy Density Report:  Show energy usage in W/sq ft.

        - Activity Report: Show what activity has taken place over a period of time for one or more areas. Activity includes occupant activities (e.g. wall controls being pressed), building manager operation (e.g. controlling/changing areas using the control and monitor tool), and device failures (e.g. keypads or ballasts that are not responding).

        - Lamp Failure Report: Shows which areas are currently reporting lamp failures.

        - Alert Activity Report: Capable of generating historical reports of all alert activity within the system.

      - Alerts and Alarms: Monitors the system for designated events/triggers and automatically generates alerts according to configured response criteria.

        - Capable of monitoring for the following events/triggers:

          - A failed piece of equipment (e.g. ballast, control, sensor, etc.); alert cleared when equipment is replaced.

          - A lamp outage (for compatible digital electronic dimming ballasts only); alert cleared when lamp is replaced.

          - Low battery conditions in battery-operated sensors and controls; alert cleared when battery is replaced.

          - Luminaires with lamp operating hours in excess of designated time.

          - Energy usage higher than designated threshold target.

          - Potential sensor failures.

          - Supported HVAC alerts when controlled by Lutron Palladiom thermostats.

        - View alerts across all guestrooms on a single dashboard.

        - Capable of generating alerts through visible changes in software or through email messages.

        - Capable of customizing the frequency of alerts and providing notifications immediately or through daily, weekly, or monthly summaries.

        - Capable of sending different alerts to different system users.

        - Capable of generating historical reports of all alert activity within the system.

      - Administration:

        - Users: Allows new user accounts to be created and existing user accounts to be edited.

          - Supports up to 20 concurrent users and up to 10,000 user accounts.

          - Supports Active Directory (LDAP) tying user accounts to network accounts.

        - Area and feature access can be restricted based on login credentials with assigned levels of access rights (Monitor, Control Only, Control and Edit, Admin) and customized access levels available.

      - Variables:  Used for custom program of a system and/or to signal a third party system. Any change may cause a change in the behavior of the system.

        - View the current state of system variables across subsystems.

        - Update the current variable state across all subsystems.

    - BACnet Software License:

      - Product:  Lutron Model LMR-BAC-PR (one license required for each guestroom).

      - Enables guestroom control system to communicate by means of native BACnet IP communication (does not require interface) system through a user-supplied Ethernet network.

      - Control system to be BACnet Test Laboratory (BTL) listed.

      - Enables third-party hospitality building management system to control and monitor lighting, shades/draperies, temperature, room occupancy and vacancy status, and identify system faults.

      - Available information includes, but is not limited to:

        - Any lights on.

        - All lights off.

        - Shades levels.

        - Shades closed.

        - Room temperature.

        - Temperature setpoints.

        - Thermostat alarms.

        - Lighting and HVAC power data.

        - Device statuses.

    - Micros Opera Hotel Property Management System Interface Software License:

      - Product:  Lutron Model LMR-OPERA-PR (requires on-site computer and one license for each guestroom).

      - Unless otherwise indicated, computer(s) to be provided <<by others, meeting Lighting Control Manufacturer's minimum requirements; by Lighting Control Manufacturer; or __________>>.

      - Interprets and converts information from Micros Opera hotel property management system for use by guestroom control system:

        - Guest check-in.

        - Guest check-out.

        - Guest message pending on/off.

        - Room HVAC operating mode.

        - Guest do-not-disturb on/off.

      - Interprets and converts information from guestroom control system for use by Micros Opera hotel property management system (requires Micros Guest Services Module):

        - Guest make-up-room on/off.

        - Guest do-not-disturb on/off.

      - Supports up to 10,000 guestrooms.

      - Supports advanced sequence of operations including, but not limited to:

        - Occupancy.

        - Lighting scenes.

        - Zones.

        - HVAC controls.

        - Shades.

    - Protel Hotel Property Management System Interface Software License:

      - Product:  Lutron Model LMR-PROTEL-PR (requires on-site computer and one license for each guestroom).

      - Unless otherwise indicated, computer(s) to be provided <<by others, meeting Lighting Control Manufacturer's minimum requirements; by Lighting Control Manufacturer; or __________>>.

      - Interprets and converts information from Protel hotel property management system for use by guestroom control system:

        - Guest check-in.

        - Guest check-out.

        - Guest message pending on/off.

        - Room HVAC operating mode.

        - Guest do-not-disturb on/off.

      - Interprets and converts information from guestroom control system for use by Protel hotel property management system:

        - Guest do-not-disturb on/off.

      - Supports up to 10,000 guestrooms.

      - Supports advanced sequence of operations including, but not limited to:

        - Occupancy.

        - Lighting scenes.

        - Zones.

        - HVAC controls.

        - Shades.

    - Hilton PMS Hotel Property Management System Interface Software License:

      - Product:  Lutron Model LMR-HLTNPMS-PR (requires on-site computer and one license for each guestroom).

      - Unless otherwise indicated, computer(s) to be provided <<by others, meeting Lighting Control Manufacturer's minimum requirements; by Lighting Control Manufacturer; or __________>>.

      - Interprets and converts information from Hilton PMS hotel property management system for use by guestroom control system:

        - Guest check-in.

        - Guest check-out.

      - Supports up to 10,000 guestrooms.

      - Supports advanced sequence of operations including, but not limited to:

        - Occupancy.

        - Lighting scenes.

        - Zones.

        - HVAC controls.

        - Shades.

    - Door Lock System Interface Software License:

Lutron Door Lock System Interface Software enables integration between Lutron myRoom Plus systems and popular online door lock systems including:

• KABA Saflok Systems

• Salto Systems

• VingCard Systems

      - Product:  Lutron Door Lock Interface Software License (requires on-site computer and one license for each guestroom control unit).

      - Unless otherwise indicated, computer(s) to be provided <<by others, meeting Lighting Control Manufacturer's minimum requirements; by Lighting Control Manufacturer; or __________>>.

      - Enables compatible <<KABA Saflok, Salto, or Vingcard; or _________>> online door lock system to communicate door event messages over a user-supplied Ethernet network for use by guestroom control system.

    - HotSOS/REX Hotel Service Management System Interface Software License:

      - Product:  Lutron Model LMR-HOTSOS-PR (requires on-site computer and one license for each guestroom).

      - Unless otherwise indicated, computer(s) to be provided <<by others, meeting Lighting Control Manufacturer's minimum requirements; by Lighting Control Manufacturer; or __________>>.

      - Enables guestroom control system to communicate service messages over a user supplied Ethernet network for use by compatible HotSOS/REX hotel service management system.

      - Supports the following service commands:

        - Make up room (true/false).

        - Do not disturb (true/false).

        - Guest in room (true/false).

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

  - RADIO FREQUENCY (RF) REPEATERS

HomeWorks QS Hybrid Repeaters add wireless Radio Frequency (RF) communication and extend the range of RF signals that are sent between devices.

    - Product:  Lutron Model HQR-REP-120 HomeWorks QS Hybrid Repeater.

    - Provide RF repeaters as indicated or as required to facilitate wireless communication between guestroom control unit and all wireless devices provided.

    - Communications:

      - Wired Communications:  Utilize RS485 wiring for wireless link extension up to 1000 feet between guestroom control unit and repeater or between repeaters.

      - Wireless Communications:  Communicates directly to compatible RF devices and other RF repeaters through use of a radio frequency communications link; RF range of 30 feet (9 m) between repeater and devices and 60 feet (18 m) between repeaters.

    - Provides wireless communication capability for guestroom control system via wired communication link.

    - Extends wireless communication range via connection of up to four total repeaters per communications link.

  - CONTROL STATIONS

    - Provide control stations with configuration as indicated or as required to control the loads as indicated.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

    - Privacy Controls; Lutron Pico Privacy Control:

      - Product:  Lutron Model QSWP-DM.

      - Button press enables guest to initiate or cancel make-up-room and do-not-disturb requests.

      - Power:  Class 2 (low voltage).

      - Communications:  Utilize RS485 wiring for low-voltage communications link.

      - Mounting:  Wallbox; provide wall plates with concealed mounting hardware.

      - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Black; As indicated on drawings; or __________>>.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

    - Corridor Controls; Lutron Pico Corridor Control:

      - Product:  Lutron Model QSWP-CP.

      - Indicates status of guest make-up-room and do-not-disturb-requests.

      - Button press provides doorbell functionality.

      - Power:  Class 2 (low voltage).

      - Communications:  Utilize RS485 wiring for low-voltage communications link.

      - Mounting:  Wallbox; provide wall plates with concealed mounting hardware.

      - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Black; As indicated on drawings; or __________>>.

    - Keypads:

      - General Requirements:

        - Allows control of any devices part of the guestroom control system.

Controls can be programmed with different functionality through system software without any hardware changes.

        - Allows for easy reprogramming without replacing unit.

        - Buttons/Engraving:

To help occupants understand how to use the guestroom control system, engraving requirements should be included for all controls. Engraving details should include text size and style.

          - Engrave keypads with button, zone, and scene descriptions <<as indicated on the drawings; to be selected by Architect; or _________>>.

Engraving must be durable when exposed to cleaning and normal wear.

          - Borders, logos, and graduations to use laser engraving or silk-screened graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

Unlike traditional scene control wall stations, centralized low voltage controls can be programmed so that the buttons can have a variety of functions.

        - Software Configuration:

          - Customizable keypad button functionality:

            - Buttons can be programmed to perform single defined action.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

            - Buttons can be programmed to perform defined action on press and defined action on release.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

            - Buttons can be programmed to perform automatic sequence of defined actions.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

            - Capable of deactivating select keypads to prevent accidental changes to light levels.

            - Buttons can be programmed for raise/lower of defined loads.

            - Buttons can be programmed to toggle defined set of loads on/off.

        - Status LEDs:

Time delays inherent in large systems can cause short delays between button press and system confirmation. To avoid any confusion and prevent multiple button presses, keypads should immediately show that the button has been pressed for visual confirmation.

          - Upon button press, LEDs to immediately illuminate.

There are two types of keypads; those that only send signals and those that send and receive signals. Having the latter type allows feedback to the user to verify that the request has been received and processed. If the lighting control system fails to process the button press request, the LED will turn off to indicate the true system status.

          - LEDs to reflect the true system status. LEDs to remain illuminated if the button press was properly processed or LEDs to turn off if the button press was not processed.

          - Support logic that defines when LED is illuminated:

            - Scene logic (logic is true when all zones are at defined levels).

            - Room logic (logic is true when at least one zone is on).

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

            - Pathway logic (logic is true when at least one zone is on).

      - Wired Keypads; Lutron QS Wired Palladiom Wallstations:

Architectural style wallstations are rectangular, single column. International style wallstations are square, single or double column.

        - Style:  <<Architectural Style; International Style>>.

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

To provide a clean, minimalist appearance, Palladiom wallstations feature buttons that are flush with the faceplate with minimal gaps and buttons/faceplates with matching material/finishes.

        - Buttons and Faceplate:

          - Buttons to be greater than 0.65 inch (16.5 mm) in height to provide large target area for ease of use and actuation.

          - Front of buttons to be flush with faceplate.

          - Buttons and faceplate to be of the same material and finish (e.g. plastic/plastic, glass/glass, metal/metal).

          - Buttons to depress and provide tactile feedback of a successful button push. Controls utilizing capacitive or resistive touch technology are not acceptable.

          - Gaps to be less than 0.007 inch (0.18 mm) between buttons and less than 0.15 inch (3.8 mm) between buttons and faceplate.

Include the following paragraph to specify optional button/engraving backlighting.

        - Button/Engraving Backlighting:

          - Backlighting to be visible through engraved text to provide clear readability in a variety of lighting conditions.

          - Indicate active scene or room status through the intensity of the backlighting (brighter backlit text indicates the active state).

          - Backlight intensity adjustable via programming software; capable of dynamic adjustment during usage based on conditional logic (time of day, button press, etc.).

        - Design keypads to allow field-customization of button color and engraving using field-changeable replacement kits.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

seeTouch QS Keypads::

• Available in several button configurations and finishes

• Receive up to two contact closure inputs

• LEDs on each button are used during programming and provide feedback when the buttons are pressed

• Large, rounded, backlit buttons with optional engraving

      - Wired Keypads; Lutron HomeWorks QS Wired seeTouch Keypads:

Architectural series keypads use Lutron Nova T* wall plates and are available in insert and non-insert styles. The insert style allows decorator-style controls to be easily ganged. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Style:  <<Architectural Non-Insert Style; Architectural Insert Style; Designer Style>>.

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox or low-voltage mounting bracket; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

Architrave Keypads:

• Available in several button configurations and finishes

• Receives up to two contact closure inputs

• LEDs next to each button are used during programming and provide feedback when the buttons are pressed

• Available with green status and backlight LEDs

      - Wired Keypads; Lutron HomeWorks QS Wired Architrave Keypads:

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; Lutron Architrave Wallbox; provide wall plates with concealed mounting hardware.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

Signature Series Keypads:

• Available in several button configurations and finishes

• Receive up to two contact closure inputs

• LEDs on each button are used during programming and provide feedback when the buttons are pressed

• Large, rounded, backlit buttons with option engraving

• Available with either Green or Blue status and backlight LEDs

      - Wired Keypads; Lutron HomeWorks QS Wired Signature Series Keypads:

        - Power: Class 2 (low voltage).

        - Communications: Utilize RS485 wiring for low-voltage communications link.

        - Mounting: Wallbox; Lutron Signature Series Wallbox; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Contact Closure Interface: Provide two contact closure inputs on back of unit which provide independent functions from front buttons; accepts both momentary and maintained contact closures.

        - Terminal block inputs to be over-voltage and miswire-protected against wire reversals and shorts.

        - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - Wireless Keypads; Lutron HomeWorks QS RF seeTouch Keypads:

Architectural series keypads use Lutron Nova T* wall plates. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Style:  <<Designer Style; Architectural Style>>.

        - Power: 120 VAC, 60 Hz; provide connection as indicated or as required.

        - Communications: Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

Architectural series keypads use Lutron Nova T* wall plates. Designer series keypads use Lutron Designer (Claro or Satin Colors) wall plates.

        - Mounting: Wallbox; provide wall plates with concealed mounting hardware.

        - Button/Engraving Backlighting:

          - Utilize backlighting for buttons and associated engraving to provide readability under all light conditions.

          - Backlight intensity adjustable via programming software.

        - Design keypads to allow field-customization of button color, configuration, and engraving using field-changeable replacement kits.

        - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

The Pico Wireless Control is a flexible and easy to use device that allows the user to control dimmers and switches. The Pico wireless control can function as a tabletop control on a pedestal, a lightweight handheld remote, or it can be wall-mounted with or without a Lutron Claro faceplate, to mimic a traditional keypad. The battery-operated control requires no external power or communication wiring. Models are available with integral night light.

    - Wireless (Radio Frequency) Controls; Lutron Pico Wireless Controls:

      - Product(s):

        - <<Type _____ - >>2-Button Control; Lutron Pico Wireless Control Model PJ2-2B.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>2-Button Control with Night Light; Lutron Pico Wireless Control Model PJN-2B.

        - <<Type _____ - >>2-Button with Raise/Lower Control; Lutron Pico Wireless Control Model PJ2-2BRL.

          - Button Marking:  <<Light (icons); Shade (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button Control; Lutron Pico Wireless Control Model PJ2-3B.

          - Button Marking:  <<Light (icons); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control; Lutron Pico Wireless Control Model PJ2-3BRL.

          - Button Marking:  <<Light (icons); Shade (text); Shade (icons); Blackout (text); Sheer (text); Drapery (text); As indicated on drawings; or __________>>.

        - <<Type _____ - >>3-Button with Raise/Lower Control and Night Light; Lutron Pico Wireless Control Model PJN-3BRL.

        - <<Type _____ - >>4-Button; Lutron Pico Wireless Control Model PJ2-4B.

          - Button Marking:  <<Zone controls (light); Zone controls (shade); Scene keypads (light); Scene keypads (shade); 2-group controllers (lights); 2-group controllers (shades); 2-group controllers (light and shade); 4-group toggle; As indicated on drawings; or __________>>.

        - Single Pedestal; Lutron Pico Pedestal Model L-PED1.

        - Double Pedestal; Lutron Pico Pedestal Model L-PED2.

        - Triple Pedestal; Lutron Pico Pedestal Model L-PED3.

        - Quadruple Pedestal; Lutron Pico Pedestal Model L-PED4.

        - Screw Mounting Kit; Lutron Model PICO-SM-KIT.

        - Wallbox Adapter; Lutron Model PICO-WBX-ADAPT.

      - Quantity: <<As indicated on the drawings; To be determined; provide allowance for _____ control(s); or _________>>.

      - Communicates via radio frequency to compatible devices.

      - Does not require external power packs, power or communication wiring.

Controls can be programmed with different functionality through system software without any hardware changes.

      - Allows for easy reprogramming without replacing unit.

      - Button Programming:

        - Single action.

        - Toggle action

        - Buttons can be programmed for raise/lower of defined loads.

      - Includes LED to indicate button press or programming mode status.

      - Mounting:

        - Capable of being mounted with a table stand or directly to a wall under a faceplate.

        - Faceplates: Provide concealed mounting hardware.

      - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White; Black; Ivory; Light Almond; White/Grey; As indicated on drawings; To be selected by Architect; or __________>>.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

  - PRESET CONTROLS WITH ZONE OVERRIDE

      - Product(s):

        - Preset controls with wired communications link; Lutron GRAFIK Eye QS.

        - Preset controls with wired or wireless communications link; Lutron GRAFIK EYE QS Wireless.

        - Preset controls with wired communications link and digital fixture control; Lutron GRAFIK Eye QS with EcoSystem.

        - Preset controls with wired or wireless communications link and digital fixture control; Lutron GRAFIK Eye QS Wireless with EcoSystem.

      - Provide preset controls with configuration and quantity of zones as indicated or as required to control the loads as indicated.

      - Wired Communications:  Utilize RS485 wiring for low-voltage communications link.

      - Wireless Communications:  Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; RF range of 30 feet (9 m).

      - Digital Fixture Control:

        - Electronically link a digital ballast/LED driver to a zone for both dimming and turning on/off.

        - Single integral controller with Class 1 or Class 2 isolated digital output signal conforming to IEC 60929; capable of direct control without interface.

A surge protector is sold as an accessory to a computer purchase to protect it from lightning strikes or other voltage surges. Likewise, dimmer circuits require surge protection. Surge protection can be built into a dimmer circuit or it can be purchased separately as an external accessory. Include the following paragraph to ensure that the surge protection is built into the dimming system.

      - Surge Tolerance: Designed and tested to withstand surges of 6,000 V, 3,000 amps according to IEEE C62.41.2 and IEC 61000-4-5 without impairment to performance.

      - Finish: <<As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; Standard white with white top door, unless otherwise indicated; Standard white with translucent top door, unless otherwise indicated; Customer colors to be selected by Architect; As indicated on drawings; or __________>>.

To help occupants understand how to use the lighting control system, engraving requirements should be included for all controls. Engraving details should include text size and style.

      - Engrave units with button, zone, and scene descriptions <<As indicated on drawings; To be selected by Architect; or __________>>.

      - Preset Lighting Control with Zone Override:

        - Intensity for each zone indicated by means of one illuminated bar graph per zone.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock. It is common for this leakage current to exceed 5 milliamps (the UL limit for GFCI outlets). Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

        - Utilize air gap off to disconnect the load from line supply.

        - Light intensity with real time energy savings by digital display.

        - Fade time indicated by digital display for current scene while fading.

        - For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

Only include the following paragraph if direct control of motorized shades from unit is required.

      - Preset Window Treatment Control with Zone Override:

        - Preset Expandable Window Treatment Control: Provide up to three columns of window treatment control.

        - For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

  - ROOM THERMOSTATS

--CHOOSE ONLY ONE OF THE TWO PARAGRAPHS BELOW--

    - Thermostats to be 120 V, <<As specified under other sections; furnished by others; or __________>>; provided with a contact closure input capable of setting back thermostat based on output from guestroom control system.

    - Thermostats to be low-voltage, provided by Lighting Control Manufacturer for guestroom control system interface.

      - Product:  Lutron QS Wired Palladiom Room Thermostat.

      - Power:  Class 2 (low voltage).

      - Communications:  Utilize RS485 wiring for low-voltage communications link.

      - Mounting:  Wallbox; Lutron Model EBB-1-SQ.

      - Button/Display Backlighting:  Turns on when any button is pressed and turns off after 10 seconds of inactivity.

      - Temperature Setpoint/Display:

        - Temperature Setpoint:  Adjustable in 1 degree F (0.5 degree C) increments.

        - Temperature Display:  Displays in 1 degree F (0.5 degree C) increments.

        - Can be toggled between Fahrenheit and Celsius units.

      - Room Temperature Sensor:

        - Measuring Range:  32 to 120 degrees F (0 to 50 degrees C).

        - Accuracy:  Plus/minus 1 degree F at 70 degrees F (0.5 degrees C at 25 degrees C).

        - Temperature Calibration Range:  Plus/minus 5 degrees F (3 degrees C).

      - Provide integral room humidity sensor.

      - Integral Passive Infrared Occupancy Sensor:

        - Passive Infrared Sensing:  Passive infrared coupled with technology for sensing fine motions; Lutron XCT Technology. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor’s sensitivity threshold.

        - Coverage:  900 square feet (81 sq m) with mounting height of 4 feet (1.2 m); 180 degree field of view.

        - Adjustable sensitivity (high, low presets).

Palladiom devices feature matching buttons and faceplates (e.g. plastic/plastic, glass/glass, metal/metal).

      - Provide matching material/finish for buttons and wall plates.

      - Finish: << As specified for wall controls in "Device Finishes" under GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White, unless otherwise indicated; Custom colors to be selected by Architect; As indicated on drawings; or __________>>.

      - Provide HVAC interface modules as required to control HVAC system.

        - Product(s):

          - Interface for 3-speed fan and on/off valve fan coil units (FCU); Lutron Model SMC53-MYRM.

          - Interface for 0-10V fan and 0-10V valve fan coil units (FCU); Lutron Model SMC55-MYRM.

Use of wired sensors requires a sensor module (see Low-Voltage Control Interfaces below)

  - WIRED SENSORS

    - Wired Occupancy Sensors:

      - General Requirements:

        - Comply with UL 94.

The self-adaptive internal microprocessor analyzes the signals to eliminate time-consuming adjustments and callbacks found in non-intelligent sensors.

        - Self-Adaptive:  Continually adjusts sensitivity and timing to ensure optimal lighting control for any use of the space.

        - Furnished with field-adjustable controls for time delay and sensitivity to override any adaptive features.

Power dropouts occur frequently. When power is restored, the lighting system should recover quickly and automatically return to the last lighting levels. A momentary interruption (1 or 2 seconds) of power should not cause extended periods (20 seconds or more) without lighting while the system reboots and all other electrical equipment is back on.

        - Power Failure Memory:  Settings and learned parameters to be saved in non-volatile memory and not lost should power be interrupted and subsequently restored.

        - Furnished with all necessary mounting hardware and instructions.

        - Class 2 devices.

        - Ceiling-Mounted Sensors:  Indicate viewing directions on mounting bracket.

        - Wall-Mounted Sensors:  Provide swivel-mount base.

        - Color:  White.

Ceiling- and wall-mounted sensors using passive infrared (PIR) technology sense occupancy by detecting the difference between heat emitted from the human body in motion and background space. PIR sensors are good at detecting major motion and require an unobstructed line-of-sight for accurate detection. Ceiling-mounted sensors are recommended for larger open spaces with ceilings less than 12 feet high. Wall-mounted sensors are recommended for spaces with pendant fixtures, ceiling fans, or ceilings more than 12 feet high.

      - Wired Passive Infrared Sensors:

Include the following paragraph to ensure that the line-of-sight is not obstructed due to dust and other contaminants.

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

        - Ceiling-Mounted Sensors:  Provide customizable mask to block off unwanted viewing areas.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

          - <<Type _____ - >>Ceiling-Mounted Passive Infrared Sensor, 450 square feet (42 sq m); Lutron Model LOS-CIR-450-WH: Coverage of 450 square feet (42 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Passive Infrared Sensor, 1500 square feet (140 sq m); Lutron Model LOS-CIR-1500-WH: Coverage of 1500 square feet (140 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

          - <<Type _____ - >>Wall-Mounted Passive Infrared Sensor; Lutron Model LOS-WIR-WH:  Coverage of 1600 square feet (149 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 110 degree field of view.

Ceiling-mounted sensors using ultrasonic technology sense occupancy by bouncing ultrasonic sound waves (32kHz-45kHz) off objects in a space and detecting a frequency shift between emitted and reflected sound waves. Ultrasonic sensors are good at detecting minor motion and do not require an unobstructed line-of-sight. Ceiling-mounted sensors are recommended for larger open spaces with ceilings less than 12 feet high.

      - Wired Ultrasonic Sensors:

The intent of the following paragraph is to eliminate sensor cross talk and assure reliable performance.

        - Utilize an operating frequency of 32kHz or 40kHz, crystal-controlled to operate within plus/minus 0.005 percent tolerance.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

          - <<Type _____ - >>Ceiling-Mounted Ultrasonic Sensor, 500 square feet (46 sq m); Lutron Model LOS-CUS-500-WH: Coverage of 500 square feet (46 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Ultrasonic Sensor, 1000 square feet (93 sq m); Lutron Model LOS-CUS-1000-WH: Coverage of 1,000 square feet (93 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Ultrasonic Sensor, 2000 square feet (186 sq m); Lutron Model LOS-CUS-2000-WH: Coverage of 2000 square feet (186 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 360 degree field of view.

Ceiling-and wall-mounted dual technology sensors use both passive infrared and ultrasonic technologies for sensing occupancy providing maximum reliability. Ceiling-mounted sensors are recommended for larger open spaces with ceilings less than 12 feet height. Wall-mounted sensors are recommended for spaces with pendant fixtures, ceiling fans, or ceilings more than 12 feet high.

      - Wired Dual Technology Sensors:

Include the following paragraph to ensure that the line-of-sight is not obstructed due to dust and other contaminants.

        - Passive Infrared:  Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Include the following paragraph to eliminate sensor cross talk and assure reliable performance.

        - Ultrasonic:  Utilize an operating frequency of 32kHz or 40kHz, crystal-controlled to operate within plus/minus 0.005 percent tolerance.

        - Ceiling-Mounted Sensors:  Provide customizable mask to block off unwanted viewing areas.

Omit the optional choice in the following paragraph if only models with isolated relay will be used.

Contact Rating (R Models only)

SPDT 500mA rated at 24V isolated relay.

        - Isolated Relay:  Provide an internal additional isolated relay with Normally Open, Normally Closed, and Common outputs for use with HVAC control, Data Logging and other control options<< where indicated>>.

Omit the optional choice in the following paragraph if only models with integral photocell will be used.

PhotoCell (R Models only)

-Prevents light from turning on when there is sufficient natural light

-Sensitivity: 0-1,000 LUX adjustable

        - Integral Photocell:  Provide an integral photocell with adjustable sensitivity to prevent lights from turning on when there is sufficient natural light<< where indicated>>.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s), Without Isolated Relay and Integral Photocell:

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 500 square feet (46 sq m); Lutron Model LOS-CDT-500-WH: Coverage of 500 square feet (46 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 1000 square feet (93 sq m); Lutron Model LOS-CDT-1000-WH: Coverage of 1000 square feet (93 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 180 degree field of view.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 2000 square feet (186 sq m); Lutron Model LOS-CDT-2000-WH: Coverage of 2000 square feet (186 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 360 degree field of view.

          - <<Type _____ - >>Wall-Mounted Dual Technology Sensor; Lutron Model LOS-WDT-WH: Coverage of 1600 square feet (149 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 110 degree field of view.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s), With Isolated Relay and Integral Photocell:

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 500 square feet (46 sq m); Lutron Model LOS-CDT-500R-WH: Coverage of 500 square feet (46 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 180 degree field of view; with isolated relay and integral photocell.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 1000 square feet (93 sq m); Lutron Model LOS-CDT-1000R-WH: Coverage of 1000 square feet (93 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 180 degree field of view; with isolated relay and integral photocell.

          - <<Type _____ - >>Ceiling-Mounted Dual Technology Sensor, 2000 square feet (186 sq m); Lutron Model LOS-CDT-2000R-WH: Coverage of 2000 square feet (186 sq m) with ceiling height of 8 to 12 feet (2.6 to 3.7 m); 360 degree field of view; with isolated relay and integral photocell.

          - <<Type _____ - >>Wall-Mounted Dual Technology Sensor; Lutron Model LOS-WDT-R-WH:  Coverage of 1600 square feet (149 sq m) with ceiling height of 8 to 12 feet (2.4 to 3.7 m); 110 degree field of view; with isolated relay and integral photocell.

    - Sensor Power Packs:

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

      - Product(s):

        - <<Type _____ - >>120-277 VAC power input/24 VDC, 150 mA power output; 16 A lighting (120-177 V), 1 HP motor (120-277 V) relay contact rating; Lutron Model PP-DV Power Pack.

        - <<Type _____ - >>120-277 VAC power input (manual)/24 VDC, 150 mA power output; 16 A lighting (120-177 V), 1 HP motor (120-277 V) relay contact rating; Lutron Model PP-DV-M Power Pack.

        - <<Type _____ - >>Control relay only (no power input/output); requires another power pack for power and counts as one of three sensors connected to a power pack; 16 A lighting (120-277 V), 1 HP motor (120-277 V), 15 A ballast (347 V) relay contact rating; Lutron Model PP-SH Power Pack.

      - Provide sensor power packs where required for power connection to sensors.

      - For ease of mounting, installation and future service, power pack(s) to be able to mount through a 1/2 inch (16 mm) trade size knockout in a standard electrical enclosure and be an integrated, self-contained unit consisting internally of an isolated load switching control relay and a transformer to provide low-voltage power. Transformer to provide power to a minimum of three sensors.

      - Plenum-rated.

      - Control Wiring Between Sensors and Control Units:  Class 2, 18-24 AWG, stranded UL Classified, PVC insulated or TEFLON jacketed cable suitable for use in plenums, where applicable.

Use of wireless sensors with myRoom prime systems requires a sensor module (see Low-Voltage Control Interfaces below)

  - WIRELESS SENSORS

    - General Requirements:

      - Operational life of 10 years without the need to replace batteries when installed per manufacturer's instructions.

      - Communicates directly to compatible RF receiving devices through use of a radio frequency communications link.

      - Does not require external power packs, power wiring, or communication wiring.

      - Capable of being placed in test mode to verify correct operation from the face of the unit.

      - RF Range: 30 feet (9 m) between sensor and compatible RF receiving device(s).

The FCC sets limits on EMI/RFI for both non-consumer (commercial and industrial) and consumer (residential) applications. The class B, consumer limits are more stringent than the class A, non-consumer limits.

      - Electromagnetic Interference/Radio Frequency Interference (EMI/RFI) Limits:  Comply with FCC requirements of CFR, Title 47, Part 15, for Class B application.

Lutron's occupancy/vacancy sensors are wireless, battery-powered passive infrared (PIR) sensors that automatically control lights via RF communication to compatible dimming and switching devices. These sensors detect the heat from people moving within an area to determine when the space is occupied. The sensors then wirelessly transmit the appropriate commands to the associated dimming and switching devices to turn the lights on or off automatically. They combine both convenience and exceptional energy savings along with ease of installation.

    - Wireless Occupancy/Vacancy Sensors:

      - General Requirements:

        - Provides a clearly visible method of indication to verify that motion is being detected during testing and that the unit is communicating to compatible RF receiving devices.

Include the following paragraph to ensure that the line-of-sight is not obstructed due to dust and other contaminants.

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Lutron's XCT signal processing technology greatly enhances the performance of PIR sensors, enabling them to "see" fine motions that other sensors couldn't previously detect. Plus, the user-replaceable batteries are designed to last up to 10 years.

        - Sensing Mechanism:  Passive infrared coupled with technology for sensing fine motions; Lutron XCT Technology. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor's sensitivity threshold.

        - Provide optional, readily accessible, user-adjustable controls for timeout, automatic/manual-on, and sensitivity; adjustable timeout settings of 1, 5, 15 and 30 minutes.

        - Color:  White.

        - Provide all necessary mounting hardware and instructions for both temporary and permanent mounting.

        - Provide temporary mounting means to allow user to check proper performance and relocate as needed before permanently mounting sensor. Temporary mounting method to be design for easy, damage-free removal.

        - Sensor lens to illuminate during test mode when motion is detected to allow installer to verify coverage prior to permanent mounting.

        - Ceiling-Mounted Sensors:

          - Provide surface mounting bracket compatible with drywall, plaster, wood, concrete, and compressed fiber ceilings.

          - Provide recessed mounting bracket compatible with drywall and compressed fiber ceilings.

          - Provide customizable mask to block off unwanted viewing areas.

        - Wall-Mounted Sensors:  Provide wall or corner mounting brackets compatible with drywall and plaster walls.

      - Wireless Combination Occupancy/Vacancy Sensors:

-Wireless occupancy sensor has three settings available: Auto-On/Auto-Off, Auto-On Low-Light/Auto-Off, and Manual-On/Auto-Off

-Auto-On Low-Light feature will only turn lights on automatically if there is less than approximately 1 fc (10 lux) of ambient light

-Simple and intuitive adjustments available for Timeout, Auto-On, and Activity settings

-Supports advanced occupancy features, such as dependent occupancy groups and customizable occupied/unoccupied presets in some systems

-Refer to product specification submittal of receiving device to determine system limits

        - Ceiling-Mounted Sensors:  Programmable to operate as an occupancy sensor (automatic-on and automatic-off), an occupancy sensor with low light feature (automatic-on when less than one footcandle of ambient light available and automatic-off), or a vacancy sensor (manual-on and automatic-off).

-Wireless occupancy sensor has two settings available: Auto-On/Auto-Off, and Manual-On/Auto-Off

-Simple and intuitive adjustments available for Timeout, Activity, and Auto-On settings

-Supports advanced occupancy features, such as dependent occupancy groups and customizable occupied/unoccupied presets in some systems

-Refer to product specification submittal of receiving device to determine system limits

        - Wall-Mounted Sensors:  Programmable to operate as an occupancy sensor (automatic-on and automatic-off), or a vacancy sensor (manual-on and automatic-off).

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

Wireless ceiling-mounted occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology for sensing fine motion. Sensor can be auto-on/auto-off, auto-on low light/auto-off, or manual on/auto-off. Ceiling-mounted sensors are recommended for spaces with ceilings less than 12 feet high.

          - <<Type _____ - >>Ceiling-Mounted Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OCR2B-P-WH: Coverage from 324 square feet (30.2 sq m) to 676 square feet (62.4 sq m) depending on ceiling height from 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

Wireless 180 degree coverage wall-mount occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Wall-Mounted Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OWLB-P-WH: Minor motion coverage of 1500 square feet (139.4 sq m) and major motion coverage of 3000 square feet (278.7 sq m) with mounting height of 6 to 8 feet (1.6 to 2.4 m); 180 degree field of view.

Wireless 90 degree coverage corner-mount occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Corner-Mounted Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OKLB-P-WH: Minor motion coverage of 1225 square feet (113.8 sq m) and major motion coverage of 2500 square feet (232.3 sq m) with mounting height of 6 to 8 feet (1.6 to 2.4 m); 90 degree field of view.

Wireless hallway occupancy/vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor can be auto-on/auto-off or manual on/auto-off.

          - <<Type _____ - >>Hallway Occupancy/Vacancy Sensor; Lutron Radio Powr Savr Series, Model LFR2-OHLB-P-WH: Major motion coverage of up to 150 feet (45.7 m) with mounting height of 6 to 8 feet (1.6 to 2.4 m); narrow field of view.

      - Wireless Vacancy-Only Sensors:

Visit www.lutron.com for more information on California Title 24 requirements.

        - Operates only as a vacancy sensor (manual-on and automatic-off) )<< in accordance with California Title 24 requirements>>.

If more than one model is required, the optional choice can be used to assign type designations. Make sure that designations indicated on the drawings are consistent with those specified here.

        - Product(s):

Wireless ceiling-mounted vacancy sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology for sensing fine motion. Sensor is manual on/auto-off (meets California Title 24 requirements). Ceiling-mounted sensors are recommended for spaces with ceilings less than 12 feet high.

          - <<Type _____ - >>Ceiling-Mounted Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VCR2B-P-WH: Coverage from 324 square feet (30.2 sq m) to 676 square feet (62.4 sq m) depending on ceiling height from 8 to 12 feet (2.4 to 3.7 m); 360 degree field of view.

Wireless 180 degree coverage wall-mount vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Wall-Mounted Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VWLB-P-WH: Minor motion coverage of 1500 square feet (139.4 sq m) and major motion coverage of 3000 square feet (278.7 sq m) with mounting height of 6 to 8 feet (1.6 to 2.4 m); 180 degree field of view.

Wireless 90 degree coverage corner-mount vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Corner-Mounted Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VKLB-P-WH: Minor motion coverage of 1225 square feet (113.8 sq m) and major motion coverage of 2500 square feet (232.3 sq m) with mounting height of 6 to 8 feet (1.6 to 2.4 m); 90 degree field of view.

Wireless hallway vacancy-only sensor using infrared technology for sensing occupancy coupled with Lutron XCT Technology. Sensor is manual-on/auto-off (meets California Title 24 requirements).

          - <<Type _____ - >>Hallway Vacancy-Only Sensor; Lutron Radio Powr Savr Series, Model LFR2-VHLB-P-WH: Major motion coverage of up to 150 feet (45.7 m) with mounting height of 6 to 8 feet (1.6 to 2.4 m); narrow field of view.

These interfaces enable the lighting control system to receive or send a control signal to or from another system (Occupancy, A/V, shades). Include this article if control over the system through external inputs such as contact closure, Ethernet, RS232, etc. is required.

  - LOW-VOLTAGE CONTROL INTERFACES

    - Provide low-voltage control interfaces as indicated or as required to control the loads as indicated.

    - Connects to system using wired communication link.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

    - Contact Closure Interface:

      - Product:  Lutron Model QSE-IO.

      - The contact closure input device to accept both momentary and maintained contact closures.

      - The contact closure output device can be configured for maintained or pulsed outputs.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

    - RS232 and Ethernet Interface:

      - Product:  Lutron Model QSE-CI-NWK-E.

      - Provide ability to communicate via Ethernet or RS232 to audiovisual equipment, touchscreens, etc.

      - Provide control of:

        - Light scene selections.

        - Fine-tuning of light scene levels with raise/lower.

        - Window treatment group presets.

        - Fine-tuning of window treatment preset levels with raise/lower.

        - Simulate system control station button presses and releases.

      - Provide status monitoring of:

        - Light scene status.

        - Window treatment group status.

        - Control station button presses and releases.

        - Control station LEDs.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

Include the following paragraph if you require the ability to operate lighting and other equipment that uses DMX-512 protocol, such as strobes, fiber optic lighting, LED-based lamps, fogger machines, and animated characters and motorized fixtures.

    - DMX Interface:

      - Product: Lutron Model QSM-CI-DMX.

      - Provides control of 32 DMX channels.

      - Provide ability to:

        - Map a single zone intensity to a single DMX512 lighting channel.

        - Map a single zone intensity to three DMX512 channels for RGB/CMY color control.

        - Map a single zone intensity to a single DMX512 integration channel.

        - Smoothly transition from one color to another in a cross fade.

        - Automatically sequence through a variety of colors.

        - Download, program, and customize a color wheel for each unit.

The QS Sensor Module (QSM) is a ceiling-mounted device that integrates Lutron wireless and wired sensors and controls through the QS communication link.

    - Sensor Modules:

      - Product(s):

Capabilities of the following module:

Up to 4 wired sensors per module

Maximum of 10 wireless occupancy sensors

Maximum of 10 wireless controllers

Sensor Module wireless range:

60 ft (18 m) line of sight

30 ft (9 m) through walls

        - Sensor module with both wired and wireless inputs; Lutron Model QSM2-4W-C.

Capabilities of the following module:

Up to 4 wired sensors per module

        - Sensor module with wired inputs only; Lutron Model QSMX-4W-C.

Capabilities of the following module:

Maximum of 10 wireless occupancy sensors

Maximum of 10 wireless controllers

Sensor Module wireless range:

60 ft (18 m) line of sight

30 ft (9 m) through walls

        - Sensor module with wireless inputs only; Lutron Model QSM2-XW-C.

      - Wired Modules:

        - Provide wired inputs for:

          - Up to four occupancy sensors.

      - Wireless Modules:

        - Provide wireless communication inputs for:

          - Up to 10 occupancy/vacancy sensors.

          - Up to 10 wireless controllers.

        - RF Range: 30 feet (9 m) between sensor and compatible RF receiving devices.

        - RF Frequency: 434 MHz; operates in FCC governed frequency spectrum for periodic operation; continuous transmission spectrum is not permitted.

      - Communicate sensor information to wired low-voltage digital link for use by compatible devices.

  - POWER INTERFACES

    - Provide power interfaces as indicated or as required to control the loads as indicated.

    - General Requirements:

Include the following paragraph to simplify field wiring for the installation contractor and prevent the failure of the interface due to phase to phase overvoltage.

      - Phase independent of control input.

Refer to NFPA 70 (NEC) 300.22, which references UL 2043 in informational note.

      - Rated for use in air-handling spaces as defined in UL 2043.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock. It is common for this leakage current to exceed 5 milliamps (the UL limit for GFCI outlets). Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

      - Utilize air gap off to disconnect the load from line supply.

      - Diagnostics and Service:  Replacing power interface does not require re-programming of system or processor.

    - Product(s):

The following modules take phase control input and provide full circuit of forward/reverse phase control (16 amps) output. The output can be 120V or 277V. This is used for incandescent, magnetic low voltage (MLV), electronic low voltage (ELV), and neon/cold cathode.

      - Phase-Adaptive Power Module; Lutron PHPM-PA:  Provides interface for phase control input to provide full 16 A circuit output of forward/reverse phase control for compatible loads.

The following modules take phase control input and provide full circuit of control (16 amps) output to Lutron Hi-lume dimming ballasts. The output can be 120V or 277V.

      - 3-Wire Fluorescent Power Module; Lutron PHPM-3F:  Provides interface for phase control input to provide full 16 A circuit output for compatible line-voltage control fluorescent electronic dimming ballasts or LED drivers.

The following modules take phase control input and provide full circuit switching (16 amps) output. The output can be 120V or 277V. This is used for non-dim loads.

      - Switching Power Module; Lutron PHPM-SW: Provides interface for phase control or switched input to provide full 16 A circuit output of switching for compatible non-dim loads.

The following interfaces take phase control input and provide full circuit of switching and 0-10V low voltage output (16 amps) for electronic fluorescent ballasts/LED drivers.

      - Ten Volt Interface; Lutron GRX-TVI: Provides interface for phase control input to provide full 16 A circuit output of switching and 0-10 V low voltage control for compatible fluorescent electronic dimming ballasts or LED drivers.

  - LED DRIVERS

    - General Requirements:

Include the following paragraph to ensure that the driver is designed to operate at worst case environmental conditions without affecting product life.

      - Operate for at least 50,000 hours at maximum case temperature and 90 percent non-condensing relative humidity.

      - Provide thermal fold-back protection by automatically reducing power output (dimming) to protect LED driver and LED light engine/fixture from damage due to over-temperature conditions that approach or exceed the LED driver's maximum operating temperature at calibration point.

      - Provide integral recording of operating hours and maximum operating temperature to aid in troubleshooting and warranty claims.

Electrostatic charge builds up on people as a result of friction (walking across a carpet). When a person touches an electronic device, a discharge can occur and cause damage. Electrostatic discharge (ESD) testing is done according to the IEC 61000-4-2 standard (human body model). Testing should be completed on all user accessible points such as terminal blocks, buttons, and control inputs. The standard only describes how to conduct the test, which is why it is important to specify "without impairment of performance" as the pass/fail criteria.

      - Designed and tested to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

During manufacturing, ballasts are more susceptible to damage by electrostatic discharge (ESD). A facility that does not meet this requirement could have excessive defective units delivered to a job site.

      - Manufactured in a facility that employs ESD reduction practices in compliance with ANSI/ESD S20.20.

UL 8750 is a UL safety standard that covers LED drivers.

      - UL 8750 recognized or listed as applicable.

UL Type TL and UL Class P are UL ratings for an LED driver. LED drivers that are Type TL rated can be easily swapped in a fixture by the fixture manufacturer with lower re-testing time and certification cost. LED drivers that are Class P listed can be swapped without any re-testing time or certification cost.

      - UL Type TL rated or UL Class P listed where possible to allow for easier fixture evaluation and listing of different driver series.

If a driver needs to be replaced in the field, a UL recognized driver listed for field replacement under UL 1598C can be replaced with a like driver. Without a UL 1598C rating, you will either have to send the fixture back to the manufacturer or have UL re-inspect the fixture in the field. UL listed Class P drivers are also suitable for field replacement.

      - Suitable for field replacement as applicable; listed in accordance with UL 1598C or UL 8750, Class P as indicated.

A surge protector is sold as an accessory to a computer purchase to protect it from lightning strikes or other voltage surges. Likewise, dimmer circuit require surge protection. Surge protection can be built into a driver or it can be purchased separately as an external accessory. Include the following paragraph to ensure that the surge protection is built into the drivers.

      - Designed and tested to withstand Category A surges of 4,000 V according to IEEE C62.41.2 without impairment of performance.

The following means that the driver will be inaudible in a general office space (30dBA is a quiet whisper at 5 feet).

      - Class A sound rating; Inaudible in a 27 dBA ambient.

Line voltage fluctuates throughout the day as equipment (i.e. equipment or other buildings in the vicinity) come on line. Line voltage fluctuations will cause noticeable changes in light output. The driver automatically compensates for variations in voltage to provide constant light output.

      - Demonstrate no visible change in light output with a variation of plus or minus 10 percent change in line-voltage input.

      - LED drivers of the same family/series to track evenly across multiple fixtures at all light levels.

To meet the lighting density requirements of a job, the fixture OEM needs to deliver fixtures with custom lumen output levels. Programmable LED drivers allow the OEM to easily customize their fixtures. Full dimming range 100%-5% or 100%-1% must be achieved at any programmed level.

      - Offer programmable output currents in 10 mA increments within designed driver operating ranges for custom fixture length and lumen output configurations, while meeting a low-end dimming range of 100 to 0.1 percent, 100 to 1 percent or 100 to 5 percent as applicable.

The following paragraph ensures that electronic dimming drivers will meet NEMA inrush recommendations, reducing false circuit breaker tripping due to turn on inrush. NEMA 410 defines the worst case inrush current expected to be encountered in field installations, and establishes uniform testing criteria for compatibility between controls, ballasts, drivers, etc.

      - Meet NEMA 410 inrush requirements for mitigating inrush currents with solid state lighting sources.

LED drivers with fault protection ensure that a wiring mistake that results in up to 277 V being applied to the communication links on the driver will not damage the driver and require the fixture to be replaced at significant cost.

      - Employ integral fault protection up to 277 V to prevent LED driver damage or failure in the event of incorrect application of line-voltage to communication link inputs.

Sometimes, the driver cannot be installed within the fixture, e.g. a chandelier. A driver that is remote mountable allows you to place the driver in a convenient location, without affecting the dimming performance of the driver.

      - LED driver may be remote located up to 100 feet (30 m) from LED light engine depending on power outputs required and wire gauge utilized by installer.

    - 3-Wire Control:

Mis-wiring control wires and/or lamp wires can cause a driver to fail. Lutron includes fault protection circuitry in its drivers to survive common mis-wires.

      - Provide integral fault protection to prevent driver failure in the event of a mis-wire.

      - Operate from input voltage of 120 V through 277 V at 50/60 Hz.

Lutron's EcoSystem® is a commercial lighting control system that is comprised of digitally addressable dimming ballasts, controls, and environmental sensors. These components provide businesses with energy savings from 40 to 70%, while increasing space flexibility, improving occupant comfort and productivity, and reducing maintenance costs.

    - Digital Control (when used with compatible Lutron lighting control systems):

After a power interruption, the lights in the space should go back to where they were prior to the interruption without flashing to full, or requiring a manual intervention. Power failure memory prevents annoying interruption to work after a power interruption.

      - Employ power failure memory; LED driver to automatically return to the previous state/light level upon restoration of utility power.

      - Operate from input voltage of 120 V through 277 V at 50/60 Hz.

For emergency lighting applications with an ATS, the control system must turn on automatically and should not be overridden except by authorized persons.

      - Automatically go to 100 percent light output upon loss of control link voltage and lock out system commands until digital control link voltage is restored. Manufacturer to offer UL 924 compliance achievable through use of external Lutron Model LUT-ELI-3PSH interface upon request.

EcoSystem drivers are field programmable to listen to up to 32 occupant sensors, 16 daylight sensors. Each driver can be configured to respond independently to each of these inputs without knowing how the system will be configured during the design phase. Moreover, such flexibility allows for system modification via programming in lieu of wiring after installation.

      - Each driver responds independently per system maximum:

        - Up to 32 occupant sensors.

        - Up to 16 daylight sensors.

Conventional load shedding systems can be limited in their performance when the load shedding signal is sent to a dimmed circuit. For example, if a 10 percent load shedding command is sent to a circuit dimmed at 80 percent, the circuit would not respond to the command because it is already operating below the limit set by the load shedding command.

      - Responds to digital load shed command. (Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast automatically sets the maximum light output at 90 percent and lowers current light output by three percent to 27 percent).

To simplify wiring, EcoSystem digital low voltage control wiring is able to be wired as either class 1 or class 2. Class 1 wiring allows the wiring to share a conduit with power wiring (where allowed by local codes) and reduce the cost of pulling control wiring in the ceiling.

      - Digital low-voltage control wiring capable of being wired as either Class 1 or Class 2.

    - Product(s):

Hi-lume® Premier 0.1% Constant Voltage L3D0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - Digital Control, 0.1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance; Lutron Hi-lume Premier 0.1% Constant Voltage (L3D0-Series):

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black (Lutron Soft-On, Fade-to-Black™) low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates 0.25 W standby power at 120 V and 0.40 W standby power at 277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at maximum power; complies with ANSI C82.11.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected, open circuit protected, and overload protected.

        - Constant Voltage Drivers:

          - Support for cove and under-cabinet fixtures at 24 V.

            - Support LED arrays from 2 W to 96 W.

IEEE 1789 sets the minimum frequency for PWM dimming above 1250 Hz to reduce chances for any disturbance in video recording.

            - Pulse Width Modulation (PWM) dimming frequency meets IEEE 1789.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

Hi-lume® Premier 0.1% Constant Voltage L3D0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - 3-Wire Control, 0.1 Percent Dimming; Lutron Hi-lume Premier 0.1% Constant Voltage (L3D0-Series):

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at maximum power; complies with ANSI C82.11.

A Class 2 output makes it easier and cheaper to design a fixture. It also allows simpler wiring for remote mounted LED drivers.

        - UL Class 2 output designed to withstand hot swap of LED loads.

        - Driver outputs to be short circuit protected, open circuit protected, and overload protected.

        - Constant Voltage Drivers:

          - Support for cove and under-cabinet fixtures at 24 V.

            - Support LED arrays from 2 W to 96 W.

IEEE 1789 sets the minimum frequency for PWM dimming above 1250 Hz to reduce chances for any disturbance in video recording.

            - Pulse Width Modulation (PWM) dimming frequency meets IEEE 1789.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

Hi-lume® Premier 0.1% Constant Current PEQ0-Series Driver is a high-performance LED driver that provides smooth, continuous dimming down to 0.1% low end.

      - Digital Control, 0.1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance; Lutron Hi-lume Premier 0.1% Constant Current (PEQ0-Series):

        - Dimming Range:  100 to 0.1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black (Lutron Soft-On, Fade-to-Black™) low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates less than 0.5 W standby power at 120/277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120/277 V.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected and open circuit protected.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

Hi-lume® 1% (PEQ1 Series) LED Drivers provide a high-performance solution for any space, in any application, while providing smooth, continuous dimming down to 1 percent of output current.

      - Digital Control, 1 Percent Dimming with Soft-On and Fade-to-Black Low End Performance; Lutron Hi-lume Premier 1% Constant Current (PEQ1-Series):

        - Dimming Range:  100 to 1 percent measured output current.

        - Features smooth fade-to-on and fade-to-black (Lutron Soft-On, Fade-to-Black™) low end dimming performance for an incandescent-like dimming experience.

        - Typically dissipates less than 0.5 W standby power at 120/277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120/277 V.

        - Class 2 output designed to withstand hot swap of LED loads; meets UL 1310 and CSA C22.2 No. 223.

        - Driver outputs to be short circuit protected and open circuit protected.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 1.05 A to ensure a compatible driver exists.

            - Support LED arrays up to 20 W.

            - Constant Current Reduction (CCR) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

Hi-lume® 1% (LTE-Series) Driver is a high-performance LED driver that provides smooth, continuous 1% dimming for virtually any LED fixture, whether it requires constant current or constant voltage. It is the most versatile LED driver offered today due to its compatibility with a wide variety of LED arrays, multiple form factors, and numerous control options.

      - Forward Phase (Neutral Wire Required), One Percent Dimming; Lutron Hi-lume 1% (LTE-Series):

        - Dimming Range:  100 to one percent relative light output.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial and residential applications at 120 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at full output for 40 W loads; complies with ANSI C82.11.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 53 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for cove and under-cabinet fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

        - Constant Voltage Drivers:

          - Support for downlights and pendant fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for troffers, linear pendants, and linear recessed fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

            - UL listed Class P.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

          - Support for cove and under-cabinet fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

            - Meets solid state requirements for power factor, transient protection, start time, and operating frequency in Energy Star for Luminaires Version 2.0.

Hi-lume® 1% (L3D-Series) Driver is a high-performance LED driver that provides smooth, continuous 1% dimming for virtually any LED fixture, whether it requires constant current or constant voltage. It is the most versatile LED driver offered today due to its compatibility with a wide variety of LED arrays, multiple form factors, and numerous control options.

      - 3-Wire and Digital Control, One Percent Dimming; Lutron Hi-lume 1% (L3D-Series):

        - Dimming Range:  100 to one percent relative light output.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120 V or 277 V.

        - Total Harmonic Distortion (THD):  Less than 20 percent at full output for loads greater than 25 W typical (higher for select models); complies with ANSI C82.11.

        - Constant Current Drivers:

          - Support for downlights and pendant fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 53 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

          - Support for troffers, linear pendants, and linear recessed fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

          - Support for cove and under-cabinet fixtures from 200 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) or Constant Current Reduction (CCR) dimming methods available.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

        - Constant Voltage Drivers:

          - Support for downlights and pendant fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

          - Support for troffers, linear pendants, and linear recessed fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

          - Support for cove and under-cabinet fixtures from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - Pulse Width Modulation (PWM) dimming method.

A UL listed driver is approved by UL for field installation outside a fixture. The driver is required to provide an enclosed wiring compartment and methods to strain relieve wiring.

            - UL listed.

5-Series (LDE5-Series) LED Drivers provide a high-performance solution for any space, in any application, while providing smooth, continuous dimming down to 5 percent of output current.

      - Digital Control, Five Percent Dimming; Lutron 5-Series (LDE5-Series):

        - Dimming Range:  100 to five percent measured output current.

        - Typically dissipates 0.2 W standby power at 120 V and 0.3 W standby power at 277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V.

        - Constant Current Reduction (CCR) dimming method.

        - Total Harmonic Distortion (THD):  Less than 21 percent at full load; complies with ANSI C82.11.

        - Constant Current Drivers:

          - Lutron K-Case Form Factor:  Support for downlights and pendant fixtures in currents from 220 mA to 1.4 A to ensure a compatible driver exists.

            - Support LED arrays up to 40 W.

            - UL listed Class P.

          - Lutron M-Case Form Factor:  Support for troffers, linear pendants, and linear recessed fixtures from 150 mA to 2.1 A to ensure a compatible driver exists.

            - Support LED arrays up to 75 W.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in ENERGY STAR for Luminaires Version 2.0.

            - Models available to meet the DesignLights Consortium (DLC) power line quality requirements.

            - UL listed Class P.

Hi-lume® 1% Soft-on Fade-to-Black (LDE1-Series) LED Drivers provide a high-performance solution for any space, in any application, while providing smooth, continuous dimming down to 1 percent of output current.

      - Digital Control, One Percent Dimming with Soft-On and Fade-to-Black Low End Performance; Lutron Hi-lume 1% Soft-on Fade-to-Black (LDE1-Series):

        - Dimming Range:  100 to one percent measured output current.

        - Features smooth fade-to-on and fade-to-black (Lutron Soft-On, Fade-to-Black™) low end dimming performance for an incandescent-like dimming experience.

The following paragraph ensures that the LED drivers exceed Energy Star standards for standby power.

        - Typically dissipates 0.2 W standby power at 120 V and 0.3 W standby power at 277 V.

        - Complies with FCC requirements of CFR, Title 47, Part 15, for commercial applications at 120-277 V.

Constant current dimming eliminates the chance for any disturbance in video recording.

        - Employs true Constant Current Reduction (CCR) dimming method from 100 to five percent light level and Pulse Width Modulation (PWM) dimming method from five percent to off.

        - Pulse Width Modulation (PWM) frequency of 240 Hz.

        - Total Harmonic Distortion (THD):  Less than 20 percent at full output for drivers greater than 25 W; complies with ANSI C82.11.

A Class 2 output makes it easier and cheaper to design a fixture. It also allows simpler wiring for remote mounted LED drivers.

        - UL Class 2 output.

        - Driver outputs to be short circuit protected, open circuit protected, and overload protected.

        - Constant Current Drivers:

          - Lutron K-Case Form Factor:  Support for fixtures from 220 mA to 1.4 A over multiple operating ranges.

            - Support LED arrays up to 40 W.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in ENERGY STAR for Luminaires Version 2.0.

            - UL listed Class P.

          - Lutron M-Case Form Factor:  Support for fixtures from 150 mA to 2.1 A over multiple operating ranges.

            - Support LED arrays up to 75 W.

            - Meets solid state requirements for power factor, transient protection, standby power consumption, start time, and operating frequency in ENERGY STAR for Luminaires Version 2.0.

            - Models available to meet the DesignLights Consortium (DLC) power line quality requirements.

            - UL listed Class P.

  - CONTROL SYSTEM ACCESSORIES

    - Synthetic Minimum Load; Lutron Model LUT-LBX:  Provide as indicated or as required to control loads below dimmer’s minimum rating.

    - Power Supplies: Provide power supplies as indicated or as required to power system devices and accessories.

      - Product(s):

        - 30 Power Draw Unit (PDU) DIN rail-mounted power supply for compatible Lutron myRoom accessories and devices; Lutron Model MQSPS-DH-1-30.

        - Din rail-mounted power supply for Lutron myRoom guestroom control units, system devices, and interfaces with two wire harnesses pre-installed for installation inside a processor panel; Lutron Model QSPS-DH-1-75-H.

        - Din rail-mounted power supply for Lutron myRoom guestroom control units, system devices, and interfaces with two wire harnesses pre-installed for installation inside a processor panel; Lutron Model WQSPS-DH-1-75-H; TAA – Trade Agreement Act compliant.

        - Din rail-mounted power supply for Lutron myRoom system devices, and interfaces for installation in an IP 20 rated consumer panel or breaker panel integrated DIN; Lutron Model QSPS-DH-1-75.

        - Din rail-mounted power supply for Lutron myRoom system devices, and interfaces for installation in an IP 20 rated consumer panel or breaker panel integrated DIN; Lutron Model WQSPS-DH-1-75; TAA – Trade Agreement Act compliant.

        - Junction box-mounted power supply for shades, keypads, and accessories, and for providing additional low voltage power to communication link; Lutron Model QSPS-J-1-35V; with miswire and thermal protection.

        - Plug-in power supply for shades, drapery drive units, keypads, and accessories, and for providing additional low voltage power to communication link; Lutron Model QSPS-P1-1-35V; with miswire protection; powered from standard receptacle using cord 6 feet (1.8 m) in length; complies with DOE Level VI regulation.

        - Ten output power supply panel for shades, drapery drive units, keypads and accessories, and for providing additional low voltage power to communication link; Lutron Model QSPS-10PNL; no replaceable fuses required for overload/miswire protection; contains DOE Level VI Compliant power supplies.

    - Enclosures:  Provide as required to house system components.

      - Low-Voltage Enclosures:  Provide self-contained enclosed area for power feed.

        - Product:  Lutron Model LV16-120; 16 by 18 inches (40.6 by 45.7 cm), nominal; surface mounting; for mounting up to two guestroom control units or up to two system interfaces and up to four wire landing boards and two power supplies.

      - High-Voltage Enclosure; Lutron Model PD4-16-F: 16 by 18 inches (40.6 by 45.7 cm), nominal; surface mounting; for mounting up to four DIN rail power modules.

    - Wire Landing Boards; Lutron Model QS-WLB:  Provide as indicated or as required for terminating wiring.

  - Motorized DRAPERY TRACK

    - Product(s):

      - Drapery track with wired (low voltage) digital communications link; Lutron Alena QS.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - Drapery track with wireless (RF) digital communications link; Lutron Alena QS Wireless.

For myRoom plus systems, Alena drapery track without digital communications link is capable of either guestroom control system integration through contact closure interface or standalone operation via contact closure input from standalone keypad.

For myRoom prime systems, Alena drapery track without digital communications link is only capable of standalone operation via contact closure input from standalone keypad (not capable of guestroom control system integration through contact closure interface).

      - Drapery track without digital communications link; Lutron Alena.

The following paragraph can be used to define application information that might normally be indicated on the drawings.

If more than one type fabric, color, or mounting method is used, copy the following paragraph and edit accordingly. Use the optional choice to assign a unique designation for each (e.g. “Drapery Track Type A”, “Drapery Track for Guestroom 101”, etc.).

    - Motorized Drapery Track<< at __________; for __________; - Type _____; or __________>>:

Specify manufacturer's pattern name/number and coordinate with material below. Lutron does not offer fabrics for drapery panels.

      - Drapery Panel Fabric: <<______>>.

There are dozens of options for fabric material. Select general characteristics or specify actual type of material.

Common types include:

Vinyl coated polyester.

Vinyl coated fiberglass.

PVC coated fiberglass.

100% Fiberglass.

Polyester-acrylic blend.

100% recycled content thermoplastic olefin.

        - Material: <<______>>.

        - Color: As selected by Architect from manufacturer’s full range of colors.

        - Color: <<______>>.

      - Draw Type: <<Side draw; Center draw; Split draw (only available for drapery track with digital communications link); As indicated on drawings; or _________>>.

      - Track Shape: <<Straight; Simple return (only available for drapery track with digital communications link); As indicated on drawings; or _________>>.

      - Track Length: <<As indicated on drawings; ___ feet (___ m); or _________>>.

      - Mounting: <<Ceiling, surface; Ceiling, recessed in pocket; or _______>>.

    - General Requirements:

      - Fabric: Non-flammable, color-fast, impervious to heat and moisture, and able to retain its shape under normal operation.

Additional fire tests may be required by some jurisdictions.

        - Flammability: Pass NFPA 701 large and small tests.

      - Drapery Style:  << Pinch pleat, with hook and loop drapery panel attachment to carrier; Ripplefold, with snap drapery panel attachment to carrier>>.

      - Tracks:  Extruded aluminum, complete with drive belts, idler gear housings, carriers, and covers.

        - Color/Finish:  <<White; Bronze; Silver; As selected from manufacturer’s standard colors; Custom color to be selected; or ______>>.

        - Endcaps:  Color to match track.

      - Electronic Drive Units: 24 VDC, for connection to NFPA 70, Class 2 power source; size and configuration as recommended by manufacturer for the type, size, and arrangement of shades to be operated.

Noise rating is measured with the largest window treatment in the heaviest fabric.

      - Audible Noise: Maximum 44 dBA measured 3 feet (1 m) from the electronic drive unit; no audible clicks when motor starts and stops.

      - Pull-to-Start Manual Operation:  While at rest, pulling on drapery panel initiates motor operation for automatic movement to open/close limit.

Include the following paragraph for Lutron Alena QS Wireless.

Do not include the following paragraph for myRoom prime systems (myRoom plus only).

      - Integrated Wireless Communications: Communicates directly to compatible RF receiving devices through use of a radio frequency communications link; does not require communication wiring; RF range of 30 feet (9 m).

    - Accessories:

      - Brackets and Mounting Hardware: Size as recommended by manufacturer for mounting configuration and span indicated.

      - Fasteners: Non-corrosive, and as recommended by shade manufacturer.

      - Cornice:  ¾ inch (19 mm) thick fabric wrapped board with foam padding.

        - Style:  <<Straight; Lutron Shape A; Lutron Shape B; Lutron Shape C; Lutron Shape D; or _____>>.

        - Fabric:  <<Match drapery panel; or _____>>

    - Fabrication:

      - Field measure finished openings prior to ordering or fabrication.

Include the following paragraph to refer to manufacturer for tolerances or include the paragraph below to specify tolerances.

      - Dimensional Tolerances:  As recommended in writing by manufacturer.

Include the following paragraph to specify tolerances or include the paragraph above to refer to manufacturer for tolerances.

      - Dimensional Tolerances:  Fabricate drapery track to fit openings within specified tolerances.

        - Side Draw:  Extend track <<12 inches (300 mm); or ___ inches (___ mm)>> beyond jamb on draw side only and flush on other side.

        - Center or Split Draw:  Extend track <<12 inches (300 mm); or ___ inches (___ mm)>> beyond jambs on each side.

        - Vertical Dimensions - Provide <<1/2 inch (13 mm); ___ inch (___ mm)>> space between bottom of drapery panel and <<finish floor; or _______>>.

  - SOURCE QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - Factory Testing; Lutron Standard Factory Testing:

To ensure that 100 percent of the lighting control products work at installation, the manufacturer should test 100 percent of all assemblies at full rated load in the factory. This testing will assure that every product has been tested and guaranteed to work. Sampling would only prove that the samples work and should not be acceptable.

      - Perform full-function factory testing on all completed assemblies. Statistical sampling is not acceptable.

To ensure that 100 percent of the lighting control products work at installation, the manufacturer should test 100 percent of all ballasts and LED drivers at the factory.

      - Perform full-function factory testing on 100 percent of all LED drivers.

- EXECUTION

  - EXAMINATION

    - Verify that field measurements are as shown on the drawings.

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatments:

      - Examine finished openings for deficiencies that may preclude satisfactory installation.

      - If substrate preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

      - Start of installation shall be considered acceptance of substrates.

    - Verify that ratings and configurations of system components are consistent with the indicated requirements.

    - Verify that mounting surfaces are ready to receive system components.

    - Verify that conditions are satisfactory for installation prior to starting work.

  - PREPARATION

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatments:

      - Prepare surfaces using methods recommended by manufacturer for achieving best result for substrate under the project conditions.

      - Coordinate with window installation and placement of concealed blocking to support window treatments.

  - INSTALLATION

    - Perform work in a neat and workmanlike manner in accordance with NECA 1 and, where applicable, NECA 130<<, except for mounting heights specified in those standards;, including mounting heights specified in those standards unless otherwise indicated; or __________>>.

    - Install products in accordance with manufacturer's instructions.

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatment Installation:

      - Install in accordance with approved shop drawings, using mounting devices as indicated.

      - Installation Tolerance: <<1/16 inch (1.5 mm); ___ inch (___ mm)>> maximum offset from level.

      - Replace window treatments that exceed specified dimensional tolerances at no extra cost to Owner.

      - Ensure smooth window treatment operation.

In order for the system to be fully commissioned and operating to specification, a database will need to be created. It is critical that the manufacturer receive information on load and control functionality so that the database can be written and fully tested by the manufacturer.

    - Define each dimmer/relay load type, assign each load to a zone, and set control functions.

    - Sensor Locations:

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS".

      - Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS", locate sensors in accordance with layout provided by Lighting Control Manufacturer. Lighting Control Manufacturer may direct Contractor regarding sensor relocation should conditions require a deviation from locations indicated. Where Lighting Control Manufacturer Sensor Layout and Tuning service is not specified, locate sensors in accordance with Drawings.

      - Sensor locations indicated are diagrammatic. Within the design intent, reasonably minor adjustments to locations may be made in order to optimize coverage and avoid conflicts or problems affecting coverage, in accordance with manufacturer's recommendations.

Many lamp manufacturers recommend seasoning fluorescent lamps prior to dimming in order to ensure full rated life.

    - Lamp Burn-In:  Operate lamps at full output for prescribed period per manufacturer's recommendations prior to use with any dimming controls. Replace lamps that fail prematurely due to improper lamp burn-in.

If the lamp leads exceed the specification, trouble starting the lamps may result.

    - LED Light Engine/Array Lead Length: Do not exceed 100 feet (31 m).

Use the following paragraph to specify an optional visit for system and network integration consultation. Edit the second choice to have this additional value include as an alternate or as part of the base bid.

A System and Network Integration Consultation is required for a job that will integrate with a third party BMS system.

    - System and Network Integration Consultation; Lutron LSC-INT-VISIT: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to conduct meeting with facility representative and other related equipment manufacturers to discuss equipment and integration procedures.

      - Coordinate scheduling of visit with Lighting Control Manufacturer. Manufacturer recommends that this visit be scheduled early in construction phase, after system purchase but prior to system installation.

    - Identify system components << in accordance with Section 26 0553>>.

  - FIELD QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

Lutron's full-scope startup services include multiple site visits to ensure proper operation. The first site visit ensures that the contractor is trained to install the system correctly. The second visit starts up the system and ensures that the system is operating as specified. The third visit trains the owner on system operation and functionality.

    - Manufacturer's Full-Scope Startup Services; <<Lutron LSC-OSSU-MYRM-PL myRoom Plus Onsite Full-Scope Startup; or Lutron LSC-OSSU-MYRM-PR myRoom Prime Onsite Full-Scope Startup>>:

      - Manufacturer's authorized Service Representative to conduct minimum of three site visits to ensure proper system installation and operation.

      - Conduct Pre-Wire visit to review requirements with installer as specified in Part 1 under "Administrative Requirements".

      - Conduct second site visit upon completion of guestroom control system to perform system startup and verify proper operation:

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS".

        - Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under “GUESTROOM CONTROL SYSTEM – GENERAL REQUIREMENTS”, authorized Service Representative to verify sensor locations, in accordance with layout provided by Lighting Control Manufacturer; Lighting Control Manufacturer may direct Contractor regarding sensor relocation should conditions require a deviation from locations indicated.

        - Verify connection of power wiring and load circuits.

        - Verify connection and location of controls.

        - Energize guestroom control units and download system data program.

        - Address devices.

        - Verify system operation control by control.

        - Verify proper operation of manufacturer's interfacing equipment.

        - Configure initial groupings of loads for wall controls and occupancy sensors.

        - Provide initial rough calibration of sensors; fine-tuning of sensors is responsibility of Contractor unless provided by Lighting Control Manufacturer as part of Sensor Layout and Tuning service where specified in Part 2 under "GUESTROOM CONTROL SYSTEM - GENERAL REQUIREMENTS".

        - Obtain sign-off on system functions.

Include the following paragraph if start-up of lighting control system outside of normal business hours is required. Edit the choice to have this additional cost included as an alternate or as part of the base bid.

        - After Hours Startup; Lutron LSC-AH-SU: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs to perform manufacturer's startup procedures outside normal working hours (Monday through Friday, 7am to 5pm).

      - Conduct third visit to train Owner's representative on system capabilities, operation, and maintenance, as specified in Part 3 under "Closeout Activities".

    - Correct defective work, adjust for proper operation, and retest until entire system complies with contract documents.

  - ADJUSTING

Use the following paragraph to specify an optional on-site meeting with the Lighting Control Manufacturer to make adjustments to the lighting control system, after all equipment and room furnishings have been installed. Edit the first choice to have this additional value included as an alternate or as part of the base bid.

This meeting may be desired in order to meet the lighting designer's original design intent. These adjustments may include light level, fade time and delay in lighting scenes.

    - On-Site Scene and Level Tuning; Lutron LSC-AF-VISIT: Include <<as part of the base bid; as an alternate to the base bid; or _________>> additional costs for Lighting Control Manufacturer to visit site to conduct meeting with <<Engineer; Owner's representative; Lighting Designer; or __________>> to make required lighting adjustments to the system for conformance with original design intent.

Lighting Control Manufacturer Sensor Layout and Tuning service may be specified in Part 2 under "LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS".

    - Sensor Fine-Tuning: Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under “LIGHTING CONTROL SYSTEM – GENERAL REQUIREMENTS”, Lighting Control Manufacturer to provide up to two additional post-startup on-site service visits for fine-tuning of sensor calibration. Where Lighting Control Manufacturer Sensor Layout and Tuning service is not specified, Contractor to provide fine-tuning of sensor calibration.

  - CLEANING

    - Clean exposed surfaces to remove dirt, paint, or other foreign material and restore to match original factory finish.

Include the following paragraph only if specifying motorized window treatments.

    - Window Treatments:

      - Clean soiled window treatments and exposed components as recommended by manufacturer.

      - Replace window treatments that cannot be cleaned to "like new" condition.

  - COMMISSIONING

    - See Section 01 9113 – General Commissioning Requirements for commissioning requirements.

Use the following paragraph to specify that lighting control acceptance testing required by California Title 24, Part 6 (California Energy Code) be performed by Lighting Control Manufacturer. Edit the second choice to have this additional cost included as an alternate or as part of the base bid.

Required documentation associated with this service is also specified in Part 1 under “SUBMITTALS”.

    - Title 24 Acceptance Testing Service; Lutron LSC-SPV-DOC-T24: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to perform lighting control acceptance testing in accordance with CAL TITLE 24 P6. Submit required documentation.

  - CLOSEOUT ACTIVITIES

    - See Section 01 7800 - Closeout Submittals, for closeout submittals.

    - See Section 01 7900 - Demonstration and Training, for additional requirements.

    - Demonstration:

Use the following paragraph to specify an optional on-site walkthrough to demonstrate system functionality (at an additional cost). Edit the first choice to have this additional cost included as an alternate or as part of the base bid.

An on-site walkthrough to demonstrate system functionality to a commissioning agent is often required for LEED projects, other projects which involve a commissioning agent, or Title 24 (California) projects. During this visit, the manufacturer's authorized Service Representative will perform tasks, at the request of the facility representative or commissioning agent, such as to demonstrate wall control functions, explain timeclock schedules or describe occupancy or daylight sensor functionality.

      - On-Site Performance-Verification Walkthrough; Lutron LSC-WALK: Include <<as part of the base bid; as an alternate to the base bid; or __________>> additional costs for Lighting Control Manufacturer to provide on-site demonstration of system functionality to <<commissioning agent; facility representative; or __________>>.

    - Training:

Lutron's full-scope startup procedure includes training of customer representatives. Include the paragraph below to specify additional training visits.

      - Include services of manufacturer's authorized Service Representative to perform on-site training of Owner's personnel on operation, adjustment, and maintenance of lighting control system as part of manufacturer’s full-scope startup services.

Lutron's standard start-up procedure includes one day of training for customer representatives. Use the following paragraph to specify additional training visits. Edit the first choice to have this additional value included as an alternate or as part of the base bid. Edit the number of training days required according to project requirements.

      - Customer-Site Solution Training Visit; Lutron LSC-TRAINING: Include <<as part of the base bid; as an alternate to the base bid; or _________>> additional costs for Lighting Control Manufacturer to provide <<one; or _____>> day(s) of additional on-site system training.

  - PROTECTION

    - Protect installed products from subsequent construction operations.

    - Touch-up, repair or replace damaged products before Substantial Completion.

  - MAINTENANCE

    - See Section 01 7000 - Execution and Closeout Requirements, for additional requirements relating to maintenance service.

Use the following paragraph to specify an on-site meeting between the Lighting Control System Manufacturer and a facility representative to evaluate the system usage after the building has been in operation for a predetermined period of time (at an additional cost). Edit the first choice to have this additional cost included as an alternate or as part of the base bid. This evaluation can include sensor calibration, timeclock programming, light level analysis, sensor layout support, and training. Edit the time period according to project requirements.

    - System Optimization Visit; Lutron LSC-SYSOPT: Include <<as part of the base bid; as an alternate to the base bid; or _________>> additional costs for Lighting Control System Manufacturer to visit site <<six months; or __________>> after system start-up to evaluate system usage and discuss opportunities to make efficiency improvements that will fit with the current use of the facility.

END OF SECTION