SECTION 260936

MODULAR DIMMING CONTROLS

Lutron GRAFIK Eye 3000

This specification is dated March 12, 2012 and supersedes all previous Grafik 3000 specifications.

This section includes editing notes to assist the user in editing the section to suit project requirements. These notes are included as hidden text, and can be revealed or hidden by one of the following methods:

· Microsoft Word: From the pull-down menus select TOOLS, then OPTIONS. Under the tab labeled VIEW, select or deselect the HIDDEN TEXT option.

· Corel WordPerfect: From the pull-down menus select VIEW, then select or deselect the HIDDEN TEXT option.

To print a copy of the specification that includes the hidden text, (1) Select “Print” (2) Select “Options” (3a) Check the box to print hidden text. (3b) Uncheck the box to not print hidden text.

This guide specification section is intended for use in the preparation of a project specification section covering the Lutron GRAFIK Eye 3000 central dimming control system.

The following should be noted in using this specification:

· Hypertext links are included to those organizations whose standards are referenced within the text, to assist in product selection and further research. 

· Optional text requiring a selection by the user is enclosed within brackets, e.g.: “Section [090000.]"

· Items requiring user input are enclosed within brackets, e.g.: “Section [_____ - ________]."

· Optional paragraphs are separated by an "OR" statement, e.g.:

**** OR **** 

For applications outside of North America (220V – 240V, or 230V CE) please see international CSI formatted specifications at the following web link. 

http://www.lutron.com/CMS400/TechInfoPage.aspx?id=19297
PART 1  - GENERAL

1.1 SUMMARY

A. Section Includes:

1. Modular dimming control systems.

B. Related Sections:

Edit the following subparagraphs to coordinate with other sections in the Project Manual.

1. Section [122000 - Window Treatments:] Window treatments controlled by central dimming control system.

2. Section [262726 - Wiring Devices] 

3. Section [265113 – Interior Lighting Fixtures, Lamps, and Ballasts:] Fluorescent lighting ballasts controlled by central dimming control system.

4. Section [260923 – Lighting Control Devices:] Occupancy sensors used in conjunction with central dimming control system.

1.2 REFERENCES

Edit paragraphs below to include only those standards referenced elsewhere in this Section.

A. American National Standards Institute/Institute of Electrical and Electronic Engineers (ANSI/IEEE) (www.ansi.org and www.ieee.org)
1. C62.41-1991 – Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits.

B. ASTM International (ASTM) (www.astm.org)
1. D4674 -02a Standard Test Method for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Fluorescent Lighting and Window-Filtered Daylight.

C. Canadian Standards Association (CSA) (www.csa.ca)
1. CSA C22.2 # 14 Industrial Control Equipment 

2. CSA C22.2 # 184 Solid-State Lighting Controls 

3. CSA C22.2 # 156 Solid-State Speed Controls

D. International Electrotechnical Commission (www.iec.ch)
1. (IEC) 801-2 Electrostatic Discharge Testing Standard.

2. IEC/EN 60669-2-1 Switches for household and similar fixed electrical installations - electronic switches.

E. International Organization for Standardization (ISO) (www.iso.ch):
1. 9001:2000 – Quality Management Systems.

F. National Electrical Manufacturers Association (NEMA) (www.nema.org)
1. WD1 (R2005) - General Color Requirements for Wiring Devices.

G. Norma Official Mexicana (NOM).

1. NOM-003-SCFI Productos eléctricos - Especificaciones de seguridad (Electrical products - Safety Specifications) 

H. Underwriters Laboratories, Inc. (UL) (www.ul.com):

UL 489 is the UL Standard for Safety for Molded-Case Circuit Breakers, Molded-Case Switches and Circuit-Breaker Enclosures that Underwriters Laboratories uses to independently evaluate, test and List circuit breakers for use on lighting and other branch circuits in compliance with the NEC code.  It is important that circuit breakers used for branch circuit over current protection are UL 489 listed to ensure that all NEC code requirements are met. 

1. 489 (2002) - Molded-Case Circuit Breakers, Molded-Case Switches, and Circuit-Breaker Enclosures.

UL 508 is the UL Standard for Safety for Industrial Control Equipment that Underwriters Laboratories uses to independently evaluate, test and List dimmer panels.  The limited short circuit test required by this standard tests that the product fails safely in the event that the output terminals to the load are short-circuited.  This is an important safety test. 

2. 508 (1999) - Standard for Industrial Control Equipment.

UL 1472 is the Underwriters Laboratories Standard for Safety of Solid State Dimming Controls that sets limits on the amount of DC voltage a dimmer may deliver to a magnetic ballast or transformer.  UL Listed wall box dimmers must comply with this standard.  This ensures that the dimmer will not overheat the transformer.

Lutron applies this requirement in the design and testing of all the Commercial system dimming products for MLV loads as well. 

3. 1472 (1996) - Solid-State Dimming Controls.

UL 924 is the UL Standard for Safety for Emergency Lighting and Power Equipment ensures that the lighting system will meet safety requirements in emergency situations.

4. 924 (2003) - Emergency Lighting and Power Equipment

1.3 SYSTEM DESCRIPTION

Edit paragraph below retaining only those technologies required to suit project requirements.

A. Modular dimming control system 

1. Factory assembled dimming controls. [and] [interfaces and modules]

2. Low voltage [wall stations] [and] [control interfaces] [and] [sensors].

3. [Solid-state high frequency fluorescent dimming ballasts.] 

1.4 SUBMITTALS

Edit paragraph below to coordinate with other sections in the Project Manual.

A. Submit under provisions of Section [013300.] [______.]

B. Specification Conformance Document:  Indicate whether the submitted equipment:

1. Meets specification exactly as stated.

2. Meets specification via an alternate means and indicate the specific methodology used.

C. Shop Drawings; include:

1. Load schedule indicating actual connected load, load type, and voltage per circuit, circuits and their respective control zones, circuits that are on emergency, and capacity, phase, and corresponding circuit numbers.

2. Schematic of system.

D. Product Data: Catalog cut sheets with performance specifications demonstrating compliance with specified requirements.

1.5 CLOSEOUT SUBMITTALS

Lutron has enhanced startup documentation that may be purchased.  This documentation will be completed by a Lutron Services Company Representative during the startup of the Lutron lighting control system.  This documentation defines the functional test procedures to be used and the results of the onsite testing of the Lutron equipment.  A copy of this documentation will be delivered after startup completion. 

Retain paragraph below if this enhanced documentation from the Lighting Control System Manufacturer is desired to meet project requirements.

A. [Sustainable Design Closeout Documentation (LSC-LEED-DOC)

1. Lighting Control System Manufacturer to provide LEED commissioning documentation that details the start-up procedure being performed including a process to follow, details on tests performed and an area that documents any test results.]

1.6 QUALITY ASSURANCE

Edit paragraph below to indicate minimum level of experience required by lighting management control manufacturers to suit project requirements.

A. Manufacturer: Minimum [10] [__] years experience in manufacture of architectural lighting controls.

B. Manufacturer’s Quality System: Registered to ISO 9001:2000 Quality Standard, including in-house engineering for product design activities.

C. Central dimming control system: 

Edit paragraph below retaining only those standards necessary to meet project requirements.

1. Listed by [CSA] [NOM] [UL] specifically for the required loads. Provide evidence of compliance upon request.  

1.7 PROJECT CONDITIONS

A. Do not install equipment until following conditions can be maintained in spaces to receive equipment:

1. Ambient temperature: 0 degrees to 40 degrees C (32 degrees to 104 degrees F).

2. Relative humidity: Maximum 90 percent, non-condensing.

3. Lighting control system must be protected from dust during installation.

1.8 WARRANTY

Choose the Warranty that best fits the owner’s needs.  The standard Warranty is 2 years; however, an 8 year warranty is available to the owner by purchasing an Enhanced 8-year Warranty option.   

A. Provide Manufacturer’s Warranty:

1. Standard 2-year warranty, Includes:

a. 100 Percent Replacement Parts for Manufacturer Lighting System Components

b. 100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

c. First–Available Onsite or Remote Response Time

d. 24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

e. Remote Diagnostics for Applicable Systems

**** OR ****

2. Enhanced 8-year Silver Level limited parts warranty, Includes:

a. Years 1-2:

1) 100 Percent Replacement Parts for Manufacturer Lighting System Components

2) 100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

3) First-Available Onsite or Remote Response Time

4) Remote Diagnostics for Applicable Systems

b. Years 3-5:  50% Replacement Parts Coverage

c. Years 6-8:  25% Replacement Parts Coverage

d. 24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

**** OR ****

3. Enhanced 8-year Gold Level limited parts warranty, Includes:

a. Years 1-2:

1) 100 Percent Replacement Parts for Manufacturer Lighting System Components

2) 100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

3) 72-Hour Onsite or Remote Response Time

4) Annual Scheduled Preventive Maintenance Visit

5) Remote Diagnostics for Applicable Systems

b. Years 3-5:  50% Replacement Parts Coverage

c. Years 6-8:  25% Replacement Parts Coverage

d. 24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

**** OR ****

4. Enhanced 8-year Platinum Level limited parts warranty, Includes: 

a. Years 1-2:

1) 100 Percent Replacement Parts for Manufacturer Lighting System Components

2) 100 Percent Manufacturer Coverage to Troubleshoot and Diagnose a Lighting Issue

3) 24-Hour Onsite or Remote Response Time

4) Annual Scheduled Preventive Maintenance Visit

5) Remote Diagnostics for Applicable Systems

b. Years 3-5:  50% Replacement Parts Coverage

c. Years 6-8:  25% Replacement Parts Coverage

d. 24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

An upgraded full ten-year warranty is available to the owner by purchasing additional years of Technology Support Plan coverage.  Edit the paragraphs below to specify the optional coverage period to be included (3 to 8 years) in addition to the above warranty.  If the Warranty outlined above is sufficient, delete the paragraph below.  Edit level of Technology Support Plan coverage to suit project requirements by choosing Silver, Gold or Platinum Level in paragraphs below.

B. [Provide Manufacturer’s Technology Support Plan for [8] [__] years covering 100 percent parts and 100 percent Manufacturer labor and additional benefits as described below beginning 2 years after system startup completion.]

1. Silver Level Technology Support Plan, Includes:

a. 100 Percent Parts for Manufacturer Lighting System Components

b. 100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

c.  24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

d.  First-Available Onsite or Remote Response Time

d.  Remote Diagnostics for Applicable Systems

**** OR ****

2. Gold Level Technology Support Plan, Includes:

a. 100 Percent Parts for Manufacturer Lighting System Components

b. 100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

c.  24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

d.  72-Hour On-Site or Remote Response Time

e.  Annual Scheduled Preventive Maintenance Visit

f.  Remote Diagnostics for Applicable Systems 

h. Includes Service Coverage Upgrade of the Initial 2-year 100 Percent Manufacturer Warranty Labor Coverage to Gold Level Coverage.

**** OR ****

3. Platinum Level Technology Support Plan, Includes:

a. 100 Percent Parts for Manufacturer Lighting System Components 

b. 100 Percent Manufacturer Labor Coverage  to Troubleshoot and Diagnose a Lighting Issue

c.  24 Hours Per Day, 7 Days per Week Telephone Technical Support, excluding Manufacturer Holidays 

d.  24-Hour On-Site or Remote Response Time

e.  Annual Scheduled Preventive Maintenance Visit

f.  Remote Diagnostics for Applicable Systems

h.  Includes Service Coverage Upgrade of the Initial 2-Year 100 Percent Manufacturer Warranty Labor Coverage to Platinum Level Coverage.

Retain paragraph below if fluorescent dimming ballasts will be included to meet project requirements.  Edit to coordinate with other sections in the Project Manual.

C. [For ballasts, see section 265113 – Interior Lighting Fixtures, Lamps, and Ballasts.]

Retain paragraph below if Sivoia QED Shades will be included to meet project requirements.  Edit to coordinate with other sections in the Project Manual.

D. [For Sivoia QED shades, see section 122413 – Roller Window Shades: Sivoia QED.]

1.9 MAINTENANCE

A. Make ordering of new equipment for expansions, replacements, and spare parts available to end user. 

B. Make new replacement parts available for minimum of ten years from date of manufacture.

PART 2  - PRODUCTS

2.1 MANUFACTURERS

A. Acceptable Manufacturer: Lutron Electronics Co., Inc. – System: Lutron GRAFIK Eye 3000

****OR****

B. [Basis of design product: Lutron GRAFIK Eye 3000 or subject to compliance and prior approval with specified requirements of this section, one of the following:]

1. Lutron GRAFIK Eye 3000

2. <Insert manufacturer’s name>

C. Substitutions: [Not permitted.] [Under provisions of Division 1.] 

Delete items 1 through 5 if substitutions are not permitted.

1. All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by the design professional a minimum of 10 working days prior to the bid date and must be made available to all bidders.   

2. Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

3. Any substitutions provided by the contractor shall be reviewed at the contractor’s expense by the electrical engineer at a rate of [$200.00] per hour.

4. By using pre-approved substitutions, the contractor accepts responsibility and associated costs for all required modifications to circuitry, devices, and wiring.  

5. Provide complete engineered shop drawings (including power wiring) with deviations for the original design highlighted in an alternate color to the engineer for review and approval prior to rough-in.

2.2 GENERAL

The following statement ensures a single point of contact for system operation.  

A. Provide system hardware that is designed, tested, manufactured, and warranted by a single manufacturer.

Typical dimming equipment is rated for 40 degrees C (104 degrees F).   This is the maximum ambient temperature that can exist while the dimming equipment is operating at full load conditions.  The following statement ensures that the operating equipment is designed to operate at worst case environmental conditions without affecting product life.

B. Architectural Lighting Controls: Ten-year operational life while operating continually at any temperature in an ambient temperature range of 0 degrees C (32 degrees F) to 40 degrees C (104 degrees F) and 90 percent non-condensing relative humidity.  
Electrostatic charge builds up on people as a result of friction (walking across a carpet).  When a person touches an electronic device, a discharge can occur and cause damage.  Electrostatic Discharge (ESD) testing is done according to the IEC 801-2 standard (human body model).  Testing should be completed on all user accessible points such as terminal blocks, buttons, and control inputs.  The standard listed below describe only how to conduct this test, that is why it is important to specify “without impairment of performance” as the pass/fail criteria.

C. Designed and tested to withstand electrostatic discharges up to 15,000 V without impairment per IEC 801-2.

2.3 DIMMING PERFORMANCE REQUIREMENTS

Electrolytic capacitors are typically the component most sensitive to heat in a dimming circuit.  Their expected lifetime doubles for every 10 degrees C that the component operates below the capacitor’s rated operating temperature.  

(A component operated at 10 degrees C above the rated temperature will have HALF the life expectancy.  A component operated at 20 degrees C above the rated temperature will have one quarter the life expectancy.

(A component operated at 10 degrees C below the rated temperature will have DOUBLE the life expectancy. A component operated at 20 degrees C below the rated temperature will have quadruple the life expectancy.

The following statement ensures a minimum 10-year operating life under worst case field conditions.

A. Electrolytic capacitors to operate at least 20 degrees C below the component manufacturer's maximum temperature rating when device is under fully-loaded conditions in 40 degrees C (104 degrees F) ambient temperature.

Dimming equipment is exposed to peak currents much higher than rated operating current due to tungsten inrush, magnetic inrush, and lamp burnout.  If not designed to handle this inrush/surge condition, the equipment could fail at anytime when turned on or when lamps fail.  The following two statements ensure reliability of components.

B. Load Handling Thyristors (SCRs and triacs), Field Effect Transistors (FETs), and Isolated Gate Bipolar Transistors (IGBTs): Manufacturer’s maximum current rating minimum two times control’s rated operating current.

C. Capable of withstanding repetitive inrush current of 50 times operating current without impacting lifetime of dimmer.

A surge protector is sold as an accessory to a computer purchase to protect it from lighting strikes or other voltage surges.  Likewise, dimmer circuits require surge protection.  Surge protection can be built into a dimmer circuit or it can be purchased separately as an external accessory.  The following statement ensures that the surge protection is built into the dimming system.

D. Design and test dimmers to withstand line-side surges without impairment to performance.

GRAFIK Eye 3000 can be installed near electrical service entrance points which are subject to more severe surges than equipment mounted far from the electrical service entrance points.  The wall station control needs to survive surges equivalent to a Category B near lightning strike without failure.  The standards listed below describe only how to conduct this test, that is why it is important to specify “without impairment of performance” as the pass/fail criteria.

1. Control Units: Withstand surges without impairment of performance when subjected to surges of 6,000 volts, 3,000 amps per ANSI/IEEE C62.41 and per IEC 61000-4-5 surge requirements.

Other power handling devices installed on a branch circuit (far from electrical service entrance points) need to survive a Category A near lightning strike without failure.  The standards listed below describe only how to conduct this test, that is why it is important to specify “without impairment of performance” as the pass/fail criteria. 

2. Other power handling devices: Withstand surges without impairment of performance when subjected to surges of 6,000 volts, 200 amps per ANSI/IEEE C62.41.

When off, the semiconductor in a dimmer circuit can allow leakage current to the load creating the possibility for an electrical shock.  It is common for this leakage current to exceed 5 milliamps (the UL limit for a GFCI outlets).  Using an air gap eliminates leakage current by requiring a physical disconnect in the off position to prevent electric shock when servicing the load.

E. Utilize air gap off, activated when user selects “off” at any control to disconnect the load from line supply .

Power dropouts occur frequently.  When power is restored, the lighting system should recover quickly and automatically return to the last lighting levels.  A momentary interruption (1 or 2 seconds) of power should not cause extended periods (20 seconds or more) without lighting while the system reboots and all other electrical equipment is back on.  

F. Possess power failure memory such that if power is interrupted and subsequently returned, lights will automatically return to same levels (dimmed setting, full on, or off) prior to power interruption within 3 seconds.

As projects develop, loads and circuiting frequently change.  The following statement ensures that a single product can be used for a wide variety of loads.  For the customer, the system has flexibility to adapt to load and circuiting changes without changing out the equipment or losing the UL listing.  For the contractor, this allows load reconfiguration in the field without rewiring.

G. Multiple load type, tested to UL 508 to specifically control [incandescent/tungsten], [magnetic low voltage], [electronic low voltage], [neon/cold cathode], [fluorescent dimming ballasts], and [non-dim loads].

Different lighting sources such as fluorescent and incandescent require different power levels to dim from minimum to maximum.  Dimmers with too narrow a control range will not give the full dimming performance.  Dimmers with too broad a control range will have areas where changing the dimmers light level will not result in a change in light output.  Dimmers must be flexible enough to compensate for these different load types. 

H. Each dimmer to be assigned a load type that will provide a proper dimming curve for the specific light source.  

I. Possess ability to have load types assigned per circuit, configured in field.

Variations in lamp and fixture designs may require fine tuning of dimming curves.  The following statement ensures the equipment has the capability to make these adjustments.  This statement also allows facility personnel to manage the maximum light levels to achieve energy savings goals.  

J. Minimum and maximum light levels user adjustable on circuit-by-circuit basis.

Digital control systems have a fixed number of steps in their light control output.  There needs to be enough steps to ensure the human eye perceives smooth changes when moving from one light level to another.

K. Control all light sources in smooth and continuous manor. Dimmers with visible steps are not acceptable.

Utility power is subject to many sources of line noise.  Dimming equipment must maintain constant light levels in the presence of this noise.  For information see: 

Web Link: Power Quality



L. Provide real-time cycle-by-cycle compensation for incoming line voltage variations including changes in RMS voltage (plus or minus 2 percent change in RMS voltage/cycle), frequency shifts (plus or minus 2 Hz change in frequency/second), dynamic harmonics, and line noise. Systems not providing cycle-by-cycle compensation to include external power conditioning equipment to meet these requirements. 

M. Systems not providing cycle-by-cycle compensation to include external power conditioning equipment as part of dimming system. 

To minimize surge currents and extend lamp life.

N. Each dimmer to incorporate electronic "soft-start" default at initial turn-on that smoothly ramps lights up to the appropriate levels within 0.5 seconds.

O. Line Voltage Dimmers; Meet following load-specific requirements:

1. Magnetic Low Voltage (MLV) transformer:

Magnetic transformers are susceptible to overheating caused by asymmetrical input voltages. The following design requirements prevent magnetic low voltage transformers from operating above rated current and temperature under normal conditions or component failure.  

a. Contain circuitry designed to control and provide a symmetrical AC waveform to input of magnetic low voltage transformers per UL 1472, Section 5.11.

b. Dimmers using back-to-back SCR construction that could fail open causing DC power to flow into magnetic low voltage load are not acceptable.

2. Electronic Low Voltage (ELV) transformer:
Electronic transformers are susceptible to damage and audible noise issues if used with improper dimming wave forms.  Most electronic transformers require a reverse phase control wave form.  Transformer manufacturers should be able to provide detailed information on dimming requirements.

a. Dimmer to operate electronic low voltage transformers via reverse phase control.  Alternately, forward phase control dimming may be used if dimming equipment manufacturer has recommended specific ELV transformers being provided.

3. Neon and cold cathode transformers:

There are both high power factor and low power factor transformers.  Dimming is only applicable on the low power factor transformers.  Attempting to dim high power factor transformers can damage both the transformer and dimmer, and generate electrical noise on building’s electrical supply that interferes with other equipment.

a. Magnetic transformers: UL listed for use with normal (low) power factor magnetic transformers.
Electronic transformer technology is continually evolving.  At this time (July 2006) Lutron does not recommend any electronic neon transformers for dimming applications.  Lutron continues to evaluate products as they become available on the market.  Please consult with your Lutron representative for the latest technologies.

b. Electronic transformers: Must be supported by the ballast equipment manufacturer for control of specific ballasts being provided.

For fluorescent control systems consisting of different brands, consider requiring that the ballast manufacturer troubleshoot and diagnose problems after General Contractor’s “Correction after Completion” period expires.

4. Fluorescent electronic dimming ballast: Refer to Section [265113] [________] for dimming ballast specifications and performance.

P. Low Voltage Dimming Interface; Meet following requirements:

Some electronic dimming ballasts require:

(A switching circuit to apply or remove power to/from the ballast.  

(A low voltage control signal for intensity information.  

Dimming control must coordinate both of these items.

1. Coordination between low voltage dimming module and line voltage relay: Capable of being electronically linked to single zone.

IEC 60929 is a standard for electronic fluorescent ballasts, and is used by other lighting equipment controlled by low voltage signals including LED drivers and low voltage controlled neon.  It defines a specific method for 0-10V control.  

2. Single low voltage dimming module; capable of controlling following light sources:

a. 0-10V analog voltage signal.

1) Provide Class 2 isolated 0-10V output signal conforming to IEC 60929.

2) Sink current via IEC 60929. 

Retain the article below if power interfaces will be included to meet project requirements.  Edit paragraphs below based on which power interface types are necessary to suit project requirements.

Delete article below if no power interfaces will be necessary to meet project requirements.

2.4 POWER INTERFACES

PHPM-PA-xxx-WH – Power module that takes phase control input and provides provide full circuit of forward/reverse phase control (16 amps in US) output. The output can be 120V or 277V.  This is used for incandescent, magnetic low voltage (MLV), electronic low voltage (ELV), and neon/cold cathode.  See the following link for additional information:

Web Link: Phase-Adaptive Power Module





PHPM-3F-xxx-WH – Power interface that takes phase control input and provides full circuit of control (16 amps in US) output to hi-lume/eco-10 Lutron dimming ballast.  The output can be 120V or 277V.  See the following link for additional information:

Web Link: 3-Wire Fluorescent Power Module





PHPM-SW-DV-WH – Power module that takes phase control input and provides provide full circuit switching (16 amps in US) output.  The output can be 120V or 277V.  This is used for non-dim loads.  See the following link for additional information:

Web Link: Switching Power Module




NGRX-PB – Power booster that takes phase control input and provides provide full circuit of forward phase control (16 amps in US) output.  This is used for incandescent, magnetic low voltage (MLV), neon/cold cathode, and non-dim applications.  See the following link for additional information:

Web Link: NGRX-PB Power Booster




GRX-FDBI – Power interface that takes phase control input and provides full circuit of control (16 amps in US) output to hi-lume/eco-10 Lutron dimming ballast.  See the following link for additional information:

Web Link: FDBI Fluorescent Dimming Ballast Interface




GRX-ELVI - Power interface that takes phase control input and provides full circuit of control (8 amps in US) output to electronic low voltage (ELV) transformers.  See the following link for additional information:

Web Link: GRX-ELVI Electronic Low Voltage Interface




GRX-TVI – Power interface that takes phase control input and provides full circuit of switching and 0 to 10 low voltage output (16 amps in US) for electronic fluorescent ballasts.  See the following link for additional information:

Web Link: GRX-TVI Ten Volt Interface




GRX-PWM – Power interface that takes phase control input and provides full circuit of switching and pulse width modulation output.  See the following link for additional information:

Web Link: GRX-PWM Pulse Width Modulation Interface




High Power models HP-2, HP-4, HP-6 – Power booster that takes phase control input and provides provide full circuit of forward phase control (16 amps in US) output.  The phase control input is 120V and the output can be either 120V or 277V.  This is used incandescent, magnetic low voltage (MLV), neon/cold cathode, Hi-lume/eco-10, non-dim applications.  See the following link for additional information:

Web Link: Hi-Power Dimming Module




A. Product: [PHPM-PA-DV], [PHPM-PA-120], [PHPM-3F-DV], [PHPM-3F-120], [PHPM-SW-DV], [NGRX-PB.] [GRX-FDBI.] [ELVI-1000.] [GRX-TVI.] [GRX-PWM] [HP-2.], [HP-4.], [HP-6.]

B. Electrical:

This will simplify field wiring for the installation contractor and prevent the failure of the interface due to phase to phase over voltage.  

1. Phase independent of control input.

2. Dimmer to meet limited short circuit test as defined in UL 20.

C. Diagnostics and Service: Replacing power interface does not require re-programming of system or processor.

2.5 WALL STATIONS

Localized multi-zone control (LEDs & raise/lower buttons) used in applications where adjustability in the lighting level is desired.  See the following link “Preset Controls 3000 Series - Control Units” for additional information:

Web Link: GRX 3000 Series Preset Controls

A. Line Voltage Wall Stations:

1. Preset Lighting Control with Zone Override; [Lutron Grafik Eye GRX-3100] [Lutron Grafik Eye GRX-3500]:

a. Intensity for each zone indicated by means of one illuminated bar graph per zone.  

b. Fade time indicated by digital display for current scene while fading. 

c. Incorporate built-in wide angle infrared receiver.

d. For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

Edit paragraph below to indicate type of low voltage wall station controls desired to meet project requirements.  

B. Low Voltage Wall Stations:

Please see the following link for detailed product information and specification submittal sheets:

Web Link: GRAFIK Eye
seeTouch – Backlit, large rounded buttons that can be engraved and are easy to use.  

Single Button – Simple one button control for use with one or more zones of lighting.

Architectural – Thin profile buttons with LED indicator lights in an architectural style face plate.

European – Large rounded buttons LED indicator lights in a European style face plate.

Slim Button – Thin profile buttons with LED indicator lights with the ability to have up to fifteen buttons and a master on/off.

Large Button – Large profile buttons with LED indicator lights with the ability to have up to nine buttons.

Architrave – Door jamb profile with thin buttons and LED indicator lights.

Key Switch – Used in public spaces so that access can be limited to authorized access only.  See Lutron model “NTGRX-KS, Keyswitch Wallstation” in Architectural Wall Control section.

1. Product: [seeTouch.] [Single Button.] [Architectural.] [European.] [Slim Button.] [Large Button.] [Architrave.] [Key Switch.] 

2. Electronics:

The following statement provides for reliable wired communication. 

a. Use RS485 wiring for low voltage communication.

3. Functionality:

Time delays inherent in large systems can cause short delays between button press and system confirmation.  To avoid any confusion and preventing multiple button presses, keypads should immediately show that the button has been pressed for visual confirmation.

a. Upon button press, LEDs to immediately illuminate.

There are two types of keypads; those that only send signals and those that send and receive signals.  Having the latter type allows feedback to the user to verify that the request has been received and processed.  If the lighting control system fails to process the button press request, the LED will turn off to indicate the true system status.  

b. LEDs to reflect the true system status.  LEDs to remain illuminated if the button press was properly processed or the LEDs turn off if the button press was not processed.  

Controls can be programmed with different functionality through system software without any hardware changes.

c. Allow for easy reprogramming without replacing unit.

Unit will automatically reprogram without direct human interaction upon replacement.

d. Replacement of units does not require reprogramming.

e. Provide faceplates with concealed mounting hardware.

To help building occupants understand how to use the lighting control system, Architect should provide engraving requirements for all controls.   Engraving details should include text size and style.  

4. Engrave wall stations with appropriate button, zone, and scene engraving descriptions furnished prior to fabrication. 

Engraving must be durable when exposed to cleaning, and normal wear.  

5. Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

C. Color:

Edit the following to indicate desired color. For non-NEMA colors, color match coordination will be provided on request.  Please verify that your word format for item 2 below is “Delta” E “equals” 1, CIE L “asterisk” a “asterisk” b color units.  See INTERNATIONAL COMMISSION ON ILLUMINATION home page at:

Web Link: CIE



1. [Match NEMA WD1, Section 2.] [Custom color to be selected.]

Color variation in same product family: Maximum ΔE=1, CIE L*a*b color units.

2. Visible parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request. 

Provide faceplates with concealed mounting hardware.

To help building occupants understand how to use the lighting control system, Architect should provide engraving requirements for all controls.   Engraving details should include text size and style.  

D. Engrave wall stations with appropriate button, zone, and scene engraving descriptions furnished prior to fabrication. 

Engraving must be durable when exposed to cleaning, and normal wear.  

E. Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning. 

This enables the lighting control system to receive or send a control signal to or from another system (Partitioning, Occupancy, A/V, BMS, shades).  For detailed product information please see the following link:

Web Link: GRAFIK Eye

 HYPERLINK "https://www.lutron.com/exspectations/library/Contact-Closure-Interfaces/" 


Retain article below if control over the system through external inputs such as contact closure, Ethernet, RS232, building management systems (BMS), etc.is desired to meet project requirements.  Edit paragraphs below to include only those control interfaces necessary to meet project requirements.

Delete article if no control interfaces are necessary to meet project requirements.

2.6 LOW VOLTAGE CONTROL INTERFACES

A. Contact Closure Interfaces; [Lutron Model GRX-IO]

1. The contact closure input device will accept both momentary and maintained contact closures.
2. The contact closure output device can be configured for maintained or momentary outputs.
B. Contact Closure Input Interface; [Lutron Model GRX-WCI] [Lutron Model seeTouch keypads SG-xx]

1. The contact closure input device will accept both momentary and maintained contact closures.
C. Contact Closure Output Interface; [Lutron Model GRX-CCO-8]
1. The contact closure output device can be configured for maintained or momentary outputs.
D. Astronomical Timeclock and Programmer Interface; [Lutron Model GRX-CI-PRG]:

1. Provide ability to communicate by means of RS232 serial communication to GRX-4000 series system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 50 feet (15 meters) of RS232 source. 

2. Provide ability to communicate by means of TCP/IP over Ethernet to GRAFIK Eye 4000 system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 300 feet (100 meters) of Ethernet source.

An astronomical time clock automatically calculates the sunrise and sunset for any given location in the world.  The user can define automatic events in relation to daily sunrise and sunset times.  For example, the lights can turn on 30 minutes before sunset each day and turn off 30 minutes after sunrise each day.  Astronomical time clocks also automatically adjust for daylight savings time, allow for special programming for weekends, holidays, and special events.

3. Astronomical time clock and programmer interface

a. Provide access to:  

1) Scene selections.

2) Fade zone to a level.

3) Fine-tuning of preset levels with scene raise/lower.

4) Lock out scenes and zones.

5) Fine-tuning of light levels with individual zone raise/lower.

6) Enable/disable wall station.

b. Software to provide as follows:

1) System setup

a) Program low voltage controls.

b) Set up and run time clock schedules.

c) Set up and run sequences.

d) Set and report time.

e) Archive system information.

2) Provide status monitoring through button feedback and scene-status updates.

Retain paragraph below if integration to Ethernet devices such as touch screens and audio visual equipment is required.

E. Ethernet Interfaces; [Lutron Model GRX-CI-NWK-E]: RS232 Interface; [Lutron Model GRX-CI-RS232]:

1. RS232 Interface

a. Provide ability to communicate by means of RS232 serial communication to GRX-4000 series system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 15 meters (50 feet) of RS232 source. 

2. Ethernet Interface

a. Provide ability to communicate by means of TCP/IP over Ethernet to GRAFIK Eye 4000 system by means of user-supplied PC or digital audiovisual equipment. Control to be located within (1000 meters (300 feet) of Ethernet source.

3. RS232 and Ethernet Interface

a. Provide access to:  

1) Scene selections.

2) Fade zone to a level.

3) Fine-tuning of preset levels with scene raise/lower.

4) Lock out scenes and zones.

5) Fine-tuning of light levels with individual zone raise/lower.

6) Enable/disable wall station.

b. Provide status monitoring through button feedback and scene-status updates.

For integration with user supplied infrared transmitters, use the following section.  See the following link for additional information:

Web Link: GRX-IRI


F. Infrared Interface; [Lutron GRX-IRI]: 

1. Integrate third party infrared controls into preset lighting control system.

For integration with Lutron QED drives (automatic shading system), use the following section.  See the following link for additional (SIVOIA QED: SG-SVCN) information:

Web Link: Sivoia QED Controller



G. Sivoia Quiet Electronic Drive (QED) Controller; [Lutron Model SG-SVCN]: 

1. Integrate control of QED shades into preset lighting control system.

For integration with AC motor drives (automatic shading system), use the following section.  See the following link for additional (GRX-4M-GC) information:

Web Link: AC Motor Group Controller



H. AC Motor Group Controller; [Lutron Model GRX-4M-GC]: 

1. Integrate control of AC motor shades into preset lighting control system.

Radio frequency interface allows GRAFIK Eye preset lighting control to be integrated with Lutron RadioRA system.  See the following link for more information:

Web Link: RadioRA GRAFIK Eye Interface
I. Radio Frequency Interface; [Lutron Model RA-GRXI-WH]:

1. GRAFIK Eye preset lighting control to be controlled by radio frequency.

Increase energy savings in spaces with windows or skylights by automatically adjusting the lights based on the amount of available daylight.  See the following link for more information:

Web Link: DACPI Daylighting Interface
J. Automatic Daylighting Control Interface; [Lutron Model GRX-DACPI]:

1. Provide automatic scene selection in response to ambient daylight

Retain article below if sensors are needed for automated control to meet project requirements.  Edit paragraphs below to include only those sensors necessary to meet project requirements.

Delete article if no sensors are necessary to meet project requirements.

2.7 SENSORS

A ceiling mounted receiver is used in a large open room where the control point can occur at various locations throughout the room.

Web Link: Ceiling-Mounted Infrared Receiver
A. Ceiling-Mounted Infrared Receiver; [Lutron Model GRX-CIR-WH]:

1. Ceiling-Mounted Infrared Receivers have 360 degree reception of wireless infrared remote controls. 

To provide a stable day light control scheme, the sensor shall operate in an open loop fashion so that light within the space is integrated to maintain average light levels.  Closed loop sensors tend to look at fixed point and can widely fluctuate the lighting in the space depending on the status of the fixed point.  For example, a white paper on a desk can give the illusion that the space is too bright, and the closed loop sensor would dim all of the lights.  See the following link for more information:

Web Link: Daylight Sensor
B. Interior Daylight Sensors; [Lutron Model MW-FPS-WH]: 

1. Use Class 2 wiring for low voltage communication

2. Can be replaced without reprogramming

3. Open-loop basis for daylight sensor control scheme

4. Stable output over temperature from 0 degrees C to 40 degrees C

5. Partially shielded for accurate detection of available daylight to prevent fixture lighting and horizontal light component from skewing sensor detection

6. Provide linear response from 0 to 500 foot-candles

7. Constructed with plastic meeting UL94 HB

8. Mountable on lighting fixtures or recessed acoustical ceiling tiles

Glue or other chemical adhesives can become caustic or brittle at high temperatures.  EcoSystem daylight sensors and infrared receivers are constructed without the use of glue or adhesives to prevent part separation or noxious gas emissions

9. Constructed via sonic welding

10. Color:

Please verify that your word format for item 2 below is “Delta” E “equals” 1, CIE L “asterisk” a “asterisk” b color units.  See INTERNATIONAL COMMISSION ON ILLUMINATION home page at:

Web Link: CIE
a. Match NEMA WD1, Section 2 White

Color variation in same product family: Maximum ΔE=1, CIE L*a*b color units

Daylight or fluorescent lighting generate ultraviolet light which can cause parts that do not meet ASTM D4674-89 to discolor / yellow over time. 

Visible parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

Include the following section for automatic daylight control of exterior lighting.

C. Exterior Daylight Sensors:

1. Calibrated with independent turn-on and turn-off thresholds; minimum 2 foot-candles difference between the turn-on and turn-off thresholds.

2. Enclosed in weatherproof housing with shading and lens protection visor.

Include the following section for automatic detection of partition status.  Sensor will supply signal to the centralized lighting control system to automatically reconfigure the space depending upon the status of the partition.  See the following link for more information:

Web Link: Infrared Partition Sensor
D. Infrared Partition Sensor; [Lutron Model GRX-IRPS-WH]: 

1. Provide contact closure based on status of sensor.

LOS-CUS-500-WH, LOS-CUS-1000-WH, LOS-CUS-2000-WH: Ceiling mount sensors using ultrasonic technology to sense occupancy by bouncing ultrasonic sound waves (32kHz – 45kHz) off objects in a space and detecting a frequency shift between emitted and reflected sound waves.  Ultrasonic sensors are good at detecting minor motion and do not require an unobstructed line-of-sight.  Ceiling mount sensors are recommended for larger open spaces with ceilings less than 12 ft. high.

LOS-CIR-450-WH, LOS-CIR-1500-WH, LOS-WIR-WH: Ceiling and wall mount sensors using passive infrared (PIR) technology to sense occupancy by detecting the difference between heat emitted from the human body in motion and background space.  PIR sensors are good at detecting major motion and require an unobstructed line-of-sight for accurate detection.  Ceiling mount sensors are recommended for larger open spaces with ceilings less than 12 ft. high.  Wall mounted sensors are recommended for spaces with pendant fixtures, ceiling fans, or ceiling more than 12 ft. high.

LOS-CDT-500-WH, LOS-CDT-500R-WH, LOS-CDT-1000-WH, LOS-CDT-1000R-WH, LOS-CDT-2000-WH, LOS-CDT-2000R-WH, LOS-WDT-WH, LOS-WDT-R-WH: Ceiling and wall mount sensors using both passive infrared and ultrasonic technologies for sensing occupancy providing maximum reliability.  Ceiling mount sensors are recommended for larger open spaces with ceilings less than 12 ft. high.  Wall mounted sensors are recommended for spaces with pendant fixtures, ceiling fans, or ceiling more than 12 ft. high.

Web Link: Occupancy Sensors
E. Ceiling and Wall Mount Occupancy/Vacancy Sensors

1. Product: [LOS-CUS-500-WH], [LOS-CUS-1000-WH], [LOS-CUS-2000-WH], [LOS-CIR-450-WH], [LOS-CIR-1500-WH], [LOS-CDT-500-WH], [LOS-CDT-500R-WH], [LOS-CDT-1000-WH], [LOS-CDT-1000R-WH], [LOS-CDT-2000-WH], [LOS-CDT-2000R-WH], [LOS-WIR-WH], [LOS-WDT-WH], [LOS-WDT-R-WH].

2. Sensing mechanism: 

To ensure that the line of sight is not obstructed due to dust and other contaminants, the infrared sensor should be constructed as follows.

Retain subparagraph below if infrared occupancy/vacancy sensors will be necessary to meet project requirements.  Delete subparagraph if infrared occupancy/vacancy sensors will not be necessary to meet project requirements.

a. [Infrared]: Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

To eliminate sensor cross talk and assure reliable performance, the ultrasonic sensor should operate under the following parameters.

Retain subparagraph below if ultrasonic occupancy/vacancy sensors will be necessary to meet project requirements.  Delete subparagraph if ultrasonic occupancy/vacancy sensors will not be necessary to meet project requirements.

b. [Ultrasonic]: Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

Retain subparagraph below if dual technology occupancy/vacancy sensors will be necessary to meet project requirements.  Delete subparagraph if dual technology occupancy/vacancy sensors will not be necessary to meet project requirements.

c. [Dual technology]:

1) Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

2) Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

3. Sensors shall turn off or reduce lighting automatically after reasonable time delay when a room or area is vacated by the last person to occupy the space

4. Sensor shall accommodate all conditions of space utilization and all irregular work hours and habits.

Edit subparagraph below retaining only those standards necessary to meet project requirements.

5. Sensors shall be [UL], [CUL], [NOM] listed (as appropriate)

6. Sensors shall be fully adaptive and adjust their sensitivity and timing to ensure optimal lighting control for any use of the space

7. Sensors shall have field adjustable controls for time delay and sensitivity to override any adaptive features.

Power dropouts occur frequently.  When power is restored, the lighting system should recover quickly and automatically return to the last lighting levels.  A momentary interruption (1 or 2 seconds) of power should not cause extended periods (20 seconds or more) without lighting while the system reboots and all other electrical equipment is back on.  

8. Power failure memory: 

a. Controls incorporate non-volatile memory. Should power be interrupted and subsequently restored, settings and learned parameters saved in protected memory shall not be lost.

9. Provide all necessary mounting hardware and instructions.

10. Sensors shall be Class 2 devices.

11. Indicate viewing directions on mounting bracket for all Ceiling mount sensors.

12. Provide customizable mask to block off unwanted viewing areas for all ceiling mounted sensors using infrared technology.

13. Provide swivel mount base for all wall mount sensors.

14. [Provide an internal additional isolated relay with Normally Open, Normally Closed and Common outputs for use with HVAC control, Data Logging and other control options.]

F. Sensor Power Packs

1. For ease of mounting, installation and future service, power pack(s) shall be able to mount through a 1/2" knock-out in a standard electrical enclosure and be an integrated, self-contained unit consisting internally of an isolated load switching control relay and a transformer to provide low-voltage power.  Transformer shall provide power to a minimum of three (3) sensors.

2. Power pack shall be plenum rated

3. Control wiring between sensors and control units shall be Class 2, 18-24 AWG, stranded U.L. Classified, PVC insulated or TEFLON jacketed cable suitable for use in plenums, where applicable

Retain article below if accessories are needed to meet project requirements.  Edit paragraphs below to include only those accessories necessary to meet project requirements.

Delete article if no accessories are necessary to meet project requirements.

2.8 ACCESSORIES

For detailed information on emergency lighting applications, please see the following website for more information:

Web Link: Emergency Lighting Systems App Note #106



A. Emergency Lighting Interface; [Lutron LUT-ELI]

1. Provides total system listing to UL924 when used with Lutron GRAFIK Eye 4000 system. 

2. Senses all three phases of building power.

3. Provides an output to power panels if power on any phase fails.

4. Accepts a contact closure input from a fire alarm control panel.

Include the following section for controls that will be located in public spaces where the operator does not desire the public to be able to operate the lighting control.

B. Tamper Proof Covers:

1. Locking covers for preset control units and wall stations: Reversible to allow lock to be located on either side of control.

2. Compatible with IR controls.

3. Does not reduce specified IR range by more than 50 percent of its original specification.

Infrared transmitters are used with Lutron supplied infrared receiver controls.  They are used in spaces where remote control is required.  Operation is through line of sight.

C. Infrared Transmitters:

1. Provide wireless remote control capable of recalling preset light levels for [four] [eight] scenes plus “off” and of fine-tuning light levels with master raise/lower.

2. Designed for use in conjunction with compatible infrared receiver and lighting control; dependent on that receiver, not transmitter. 

3. Operate up to 15 meters (50 feet) within line-of-sight to that receiver. 

4. “Learnable” by other variable frequency remote controls.

2.9 SOURCE QUALITY CONTROL

To ensure that 100 percent of the lighting control products work at installation, the manufacturer should test 100 percent of all assemblies at full rated load in the factory.  This testing will assure that every product has been tested and guaranteed to work.  Sampling would only prove that the samples work and should not be acceptable.

A. Perform full-function testing on completed assemblies at end of line. Statistical sampling is not acceptable.

PART 3  - EXECUTION

3.1 INSTALLATION

A. Install equipment in accordance with manufacturer’s installation instructions.

B. Provide complete installation of system in accordance with Contract Documents. 

In order for the system to be fully commissioned and operating to specification, a database will need to be created.  It is critical that the manufacturer receive information on load and control functionality so that the database can be written and fully tested by the manufacture.  

C. Define each dimmer's load type, assign each load to a zone, and set control functions.

D. Provide equipment at locations and in quantities indicated on Drawings. Provide any additional equipment required to provide control intent.

In order for the exterior daylight sensor to respond to daylight during the entire daylight period, the sensor should face north so that in the morning it will see daylight from the east and in the evening it will see daylight from the west.  Directing the sensor due north also minimizes direct lighting exposure to the sensor which could overload the sensor.  

E. Mount daylight sensors to point due north with constant view of daylight.

Interior sensor work mainly with diffused light, as such, they have a much higher lighting gain than exterior sensors.  Electric light sources can affect these sensors unless the sensors are shielded from the light given off by electric light sources.

F. Ensure that daylight sensor placement minimizes sensors view of electric light sources; ceiling mounted and fixture-mounted daylight sensors shall not have direct view of luminaries.  

Retain paragraph below if an Integration Meeting is required to meet project requirements.  Delete paragraph if an Integration Meeting is not required to meet project requirements.

G. [Systems Integration:

1. Equipment Integration Meeting Visit (LSC-INT-VISIT)

a. Facility Representative to coordinate meeting between Facility Representative, Lighting Control System Manufacturer and other related equipment manufacturers to discuss equipment and integration procedures.]

To minimize construction costs and project delays, a site visit is recommended.  

3.2 SERVICE AND SUPPORT

A. Startup and Programming

Retain paragraph below if telephone startup is preferred.  If End User contact information is provided, the Standard 2-year Warranty, the covers parts and onsite diagnostic labor will be provided.  Otherwise, the warranty will be a 1-year parts only warranty.  Due to system size and other system characteristics, Lutron will quote onsite startup if required.  

1. [Provide telephone startup assistance to Electrical Contractor or End User Representative (when available, in accordance with manufacturer’s guidelines.  Otherwise, onsite startup will be utilized.)

a. Provides access to a Factory Certified Telephone Startup Technician during normal business hours.

b. Provides telephone instruction and guidance for a complete system functional test.

c. With phone startup completion and End User Registration, the 1-year parts-only warranty will be upgraded to the Standard 2-year Warranty.]

2. Provide factory-certified field service engineer to a site visit to ensure proper system installation and operation under following parameters:

a. Qualifications for factory-certified field service engineer:

1) Minimum experience of 2 years training in the electrical/electronic field.

2) Certified by the equipment manufacturer on the system installed.

b. Make a visit upon completion of installation of modular dimming control system: 

1) Verify connection of power feeds and load circuits.

2) Verify connection and location of controls.

3) Program system data.

4) Verify proper connection of digital control link.

5) Verify proper operation of manufacturers interfacing equipment.

6) Obtain sign-off on system functions.

7) User to be trained on system operation.

Due to building operations, start-up of Lighting Control System may be required outside of normal business hours (Monday through Friday, 7 a.m. to 5 p.m.).  

Retain subparagraph below if After Hours Start-up is required to meet project requirements.  Delete subparagraph if After hours Start-up is not required to meet project requirements.

3. [After Hours Start-up (LSC-AH-SU)

a. Provide factory certified Field Service Engineer to perform manufacturer’s start-up procedures outside normal working hours (Monday through Friday, 7a.m. to 5 p.m.)]

If there is a problem on the job site, the manufacturer must be reachable 24 hours per day / 7 days a week to resolve any lighting control issues.  If this service is not provided, project cost overruns and delays can occur.  Additionally, answering services can add to frustration and delays.

B. Tech Support

1. Provide factory direct technical support hotline 24 hours per day, 7 days per week.

3.3 FIELD QUALITY CONTROL

On-site adjustments to the Lighting Control System, after all equipment and room furnishings have been installed, may be desired in order to meet the Lighting Consultant’s design intent.  These adjustments may include light level, fade time and delay in lighting scenes.

Retain subparagraph below if an Aim and Focus visit is required to meet project requirements.  Specify which Facility Representative (if know) will be responsible for coordination of visit; i.e. Facility Manager, Owner, etc.

Delete subparagraph if an Aim and Focus visit is not required to meet project requirements.

A. [Manufacturer Services

1. Aim and Focus Visit (LSC-AF-VISIT)

a. Facility Representative [_______________] to coordinate on-site meeting with Lighting Control System Manufacturer and Lighting Design Consultant to make required lighting adjustments to the system for conformance with the Lighting Design Consultant’s original design intent.]

An on-site meeting between the Lighting Control System Manufacturer and a Facility Representative may be requested in advance to evaluate the system usage after the building has been in operation for a predetermined period of time.  This evaluation can include sensor calibration, timeclock programming, light level analysis, sensor layout support, and training.

Retain subparagraph below if a system optimization visit is required.  Edit the time period for this visit to suit project requirements.

2. [System Optimization Visit (LSC-SYSOPT)

a. Lighting Control System Manufacturer to visit site [6] [__] months after system start-up to evaluate system usage and discuss opportunities to make efficiency improvements that will fit with the current use of the facility.]

3.4 CLOSEOUT ACTIVITIES

Standard start-up procedure for Quantum includes training of customer representatives.  Additional training visits may be requested for reasons such as when not all required attendees are available at the same time.

Retain paragraph below if an additional training visit is required to meet project requirements.  Edit the number of additional days to meet project requirements.  Delete paragraph if additional training visits are not necessary to meet project requirements.

A. [Training Visit (LSC-TRAINING)

1. Lighting Control System Manufacturer to provide [1] [__] day additional on-site system training to site personnel.]

An on-site walkthrough to demonstrate system functionality to a Commissioning Agent is often required for LEED projects..  During this visit, the manufacturer’s Field Service Engineer will perform tasks, at the request of the facility representative or Commissioning Agent, such as to demonstrate wall control functions, explain timeclock schedules or describe occupancy and/or daylight sensor functionality.

Retain paragraph below if an on-site walkthrough between the Lighting Control System Manufacturer and a Commissioning Agent is required to meet project requirements.  Delete paragraph if an on-site walkthrough is not necessary to meet project requirements.

B. [On-site Walkthrough (LSC-WALK)

1. Lighting Control System Manufacturer to provide a factory certified Field Service Engineer to demonstrate system functionality to the Commissioning Agent.]

3.5 MAINTENANCE

A. Capable of providing on-site service support within 24 hours anywhere in continental United States and within 72 hours worldwide except where special visas are required.

B. Offer renewable service contract on yearly basis, to include parts, factory labor, and annual training visits.  Make service contracts available up to ten years after date of system startup.

END OF SECTION







Lutron
16570-

Architectural Lighting Control 

Grafik 7000


07/10/06

__________________________________________________________________________________________

Lutron

MODULAR DIMMING CONTROLS 

GRAFIK Eye 3000

10/1/2011
 

260936 - 


